## Cover sheet
Development of trajectories for residential heat decarbonisation to inform the sixth carbon budget.
A study for the Committee on Climate Change
April 2021 (N.B. Relative to version published in December 2020, some updates made to 'Fuel costs and CO2' tab only, to include corrections to the costs of heat from low carbon heat networks and biomass emissions, as well as improved labelling and streamlining to include only those assumptions used in modelling)
This workbook contains all key assumptions used in the study.
Tab colour | Contents | Description
General costs and considerations
| Financial assumptions | Discount rate, cost of capital and conversion factors
| Fuel costs and CO2 | Costs and carbon intensities of fuels for heat
Energy efficiency package costs
| Energy savings | Assumptions for energy savings from individual measures across building types
| Measures and costs | Costs for energy efficiency measures across building types
Low carbon technology cost and performance
| Technology base costs | Capex and opex of low carbon technologies
| Additional costs | Additional capex items applied for technologies under defined conditions
| Efficiencies | Efficiencies of low carbon heating systems
Technical feasibility
| Application of additional costs | Defined conditions for application of additional capex items
| Suitability matrices | Technical feasibility criteria of energy efficiency measures and low carbon heating
| Heritage cost uplifts | Cost uplifts of energy efficiency measures and low carbon heating in heritage homes
Scenario assumptions
| Scenario assumptions | Defined conditions for application of additional capex items
| Energy efficiency assumptions | Other assumptions used to determine the energy efficiency cost and savings

## Financial assumptions
Discount rate: | Standard Green book declining discount rate | Scenario
Cost of capital (domestic): | 3.5% | Balanced Net Zero Pathway / Headwinds / Widespread Engagement
Cost of capital (commercial): | 7.5% | Widespread Innovation / Tailwinds
£2019 conversion relative to £2018 | 1.0198
£2018 conversion relative to £2017 | 1.0185

## Fuel costs and CO2
Fuel costs (£/kWh) (network costs included)
Fuel type | Source | Scenario | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | Comments
Electricity for SH - Flexible | CCC | Balanced Net Zero Pathway | 0.094594 | 0.10016 | 0.099657 | 0.098661 | 0.097723 | 0.096776 | 0.095838 | 0.09442 | 0.093649 | 0.092227 | 0.090779 | 0.089401 | 0.092253 | 0.092662 | 0.093073 | 0.093475 | 0.093882 | 0.092133 | 0.090464 | 0.088866 | 0.087333 | 0.085858 | 0.084437 | 0.083063 | 0.081734 | 0.080446 | 0.079195 | 0.077978 | 0.076792 | 0.075636 | 0.074507 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403
Electricity for SH - Inflexible | CCC | Balanced Net Zero Pathway | 0.11393 | 0.11727 | 0.11697 | 0.11637 | 0.11581 | 0.11524 | 0.11468 | 0.11403 | 0.11378 | 0.11313 | 0.11246 | 0.11184 | 0.11386 | 0.11441 | 0.11496 | 0.11551 | 0.11606 | 0.11534 | 0.11466 | 0.11403 | 0.11344 | 0.11289 | 0.11236 | 0.11187 | 0.1114 | 0.11096 | 0.11053 | 0.11013 | 0.10975 | 0.10939 | 0.10904 | 0.10871 | 0.10871 | 0.10871 | 0.10871 | 0.10871 | 0.10871 | 0.10871 | 0.10871 | 0.10871 | 0.10871 | 0.10871
Electricity for SH - Highly flexible | CCC | Balanced Net Zero Pathway | 0.093479 | 0.093238 | 0.091449 | 0.089808 | 0.088225 | 0.086634 | 0.08505 | 0.084421 | 0.083792 | 0.083163 | 0.082534 | 0.081905 | 0.081276 | 0.080647 | 0.080018 | 0.079389 | 0.07876 | 0.078131 | 0.077502 | 0.076873 | 0.076244 | 0.075615 | 0.074986 | 0.074357 | 0.073728 | 0.073099 | 0.07247 | 0.071841 | 0.071212 | 0.070582 | 0.069953 | 0.069324 | 0.069324 | 0.069324 | 0.069324 | 0.069324 | 0.069324 | 0.069324 | 0.069324 | 0.069324 | 0.069324 | 0.069324
Electricity for HW - with storage | CCC | Balanced Net Zero Pathway | 0.094594 | 0.10016 | 0.099657 | 0.098661 | 0.097723 | 0.096776 | 0.095838 | 0.09442 | 0.093649 | 0.092227 | 0.090779 | 0.089401 | 0.092253 | 0.092662 | 0.093073 | 0.093475 | 0.093882 | 0.092133 | 0.090464 | 0.088866 | 0.087333 | 0.085858 | 0.084437 | 0.083063 | 0.081734 | 0.080446 | 0.079195 | 0.077978 | 0.076792 | 0.075636 | 0.074507 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403
Electricity for HW - without storage | CCC | Balanced Net Zero Pathway | 0.13639 | 0.1375 | 0.1374 | 0.1372 | 0.13701 | 0.13682 | 0.13664 | 0.13642 | 0.13633 | 0.13612 | 0.1359 | 0.13569 | 0.13636 | 0.13654 | 0.13673 | 0.13691 | 0.13709 | 0.13685 | 0.13663 | 0.13642 | 0.13622 | 0.13604 | 0.13586 | 0.1357 | 0.13554 | 0.13539 | 0.13525 | 0.13512 | 0.13499 | 0.13487 | 0.13476 | 0.13464 | 0.13464 | 0.13464 | 0.13464 | 0.13464 | 0.13464 | 0.13464 | 0.13464 | 0.13464 | 0.13464 | 0.13464
Hydrogen | CCC | Balanced Net Zero Pathway | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.12623 | 0.11506 | 0.10407 | 0.09327 | 0.082656 | 0.082546 | 0.082436 | 0.082327 | 0.082217 | 0.082107 | 0.081998 | 0.081888 | 0.081779 | 0.081669 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | Residential
Heat networks - electricity-based | CCC | Balanced Net Zero Pathway | 0.1159 | 0.1159 | 0.10778 | 0.1 | 0.092226 | 0.084447 | 0.075312 | 0.075162 | 0.075012 | 0.074862 | 0.074712 | 0.07305 | 0.074887 | 0.076724 | 0.078561 | 0.080398 | 0.081895 | 0.082909 | 0.083924 | 0.084939 | 0.085953 | 0.086569 | 0.086172 | 0.085775 | 0.085378 | 0.084981 | 0.08421 | 0.08436 | 0.084509 | 0.084659 | 0.084809 | 0.084553 | 0.084553 | 0.084553 | 0.084553 | 0.084553 | 0.084553 | 0.084553 | 0.084553 | 0.084553 | 0.084553 | 0.084553 | Represents total cost of heat, see cell D115
Electricity for SH - Flexible | CCC | Headwinds | 0.094594 | 0.10016 | 0.099657 | 0.098661 | 0.097723 | 0.096776 | 0.095838 | 0.09442 | 0.093649 | 0.092227 | 0.090779 | 0.089401 | 0.092253 | 0.092662 | 0.093073 | 0.093475 | 0.093882 | 0.092133 | 0.090464 | 0.088866 | 0.087333 | 0.085858 | 0.084437 | 0.083063 | 0.081734 | 0.080446 | 0.079195 | 0.077978 | 0.076792 | 0.075636 | 0.074507 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403
Electricity for SH - Inflexible | CCC | Headwinds | 0.11393 | 0.11727 | 0.11697 | 0.11637 | 0.11581 | 0.11524 | 0.11468 | 0.11403 | 0.11378 | 0.11313 | 0.11246 | 0.11184 | 0.11386 | 0.11441 | 0.11496 | 0.11551 | 0.11606 | 0.11534 | 0.11466 | 0.11403 | 0.11344 | 0.11289 | 0.11236 | 0.11187 | 0.1114 | 0.11096 | 0.11053 | 0.11013 | 0.10975 | 0.10939 | 0.10904 | 0.10871 | 0.10871 | 0.10871 | 0.10871 | 0.10871 | 0.10871 | 0.10871 | 0.10871 | 0.10871 | 0.10871 | 0.10871
Electricity for SH - Highly flexible | CCC | Headwinds | 0.093479 | 0.093238 | 0.091449 | 0.089808 | 0.088225 | 0.086634 | 0.08505 | 0.084421 | 0.083792 | 0.083163 | 0.082534 | 0.081905 | 0.081276 | 0.080647 | 0.080018 | 0.079389 | 0.07876 | 0.078131 | 0.077502 | 0.076873 | 0.076244 | 0.075615 | 0.074986 | 0.074357 | 0.073728 | 0.073099 | 0.07247 | 0.071841 | 0.071212 | 0.070582 | 0.069953 | 0.069324 | 0.069324 | 0.069324 | 0.069324 | 0.069324 | 0.069324 | 0.069324 | 0.069324 | 0.069324 | 0.069324 | 0.069324
Electricity for HW - with storage | CCC | Headwinds | 0.094594 | 0.10016 | 0.099657 | 0.098661 | 0.097723 | 0.096776 | 0.095838 | 0.09442 | 0.093649 | 0.092227 | 0.090779 | 0.089401 | 0.092253 | 0.092662 | 0.093073 | 0.093475 | 0.093882 | 0.092133 | 0.090464 | 0.088866 | 0.087333 | 0.085858 | 0.084437 | 0.083063 | 0.081734 | 0.080446 | 0.079195 | 0.077978 | 0.076792 | 0.075636 | 0.074507 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403 | 0.073403
Electricity for HW - without storage | CCC | Headwinds | 0.13639 | 0.1375 | 0.1374 | 0.1372 | 0.13701 | 0.13682 | 0.13664 | 0.13642 | 0.13633 | 0.13612 | 0.1359 | 0.13569 | 0.13636 | 0.13654 | 0.13673 | 0.13691 | 0.13709 | 0.13685 | 0.13663 | 0.13642 | 0.13622 | 0.13604 | 0.13586 | 0.1357 | 0.13554 | 0.13539 | 0.13525 | 0.13512 | 0.13499 | 0.13487 | 0.13476 | 0.13464 | 0.13464 | 0.13464 | 0.13464 | 0.13464 | 0.13464 | 0.13464 | 0.13464 | 0.13464 | 0.13464 | 0.13464
Hydrogen | CCC | Headwinds | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.12623 | 0.11506 | 0.10407 | 0.09327 | 0.082656 | 0.082546 | 0.082436 | 0.082327 | 0.082217 | 0.082107 | 0.081998 | 0.081888 | 0.081779 | 0.081669 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | 0.081559 | Residential
Hydrogen - High | CCC | Headwinds | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | Same as Balanced Net Zero Pathway/Headwinds till 2025, constant thereafter
Hydrogen - Low | CCC | Headwinds | 0.10644 | 0.10644 | 0.10644 | 0.10644 | 0.10644 | 0.10644 | 0.10644 | 0.098585 | 0.087414 | 0.076429 | 0.065629 | 0.055014 | 0.054904 | 0.054794 | 0.054685 | 0.054575 | 0.054466 | 0.054356 | 0.054246 | 0.054137 | 0.054027 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918 | 0.053918
Heat networks - gas to hydrogen peaking | CCC | Headwinds | 0.11124 | 0.11124 | 0.10346 | 0.095681 | 0.087903 | 0.080124 | 0.072345 | 0.072195 | 0.072046 | 0.071896 | 0.071746 | 0.071596 | 0.073433 | 0.07527 | 0.077107 | 0.078944 | 0.080926 | 0.082515 | 0.084253 | 0.085904 | 0.087995 | 0.090919 | 0.092436 | 0.093668 | 0.094279 | 0.094801 | 0.096173 | 0.096704 | 0.09734 | 0.09787 | 0.098508 | 0.099989 | 0.099989 | 0.099989 | 0.099989 | 0.099989 | 0.099989 | 0.099989 | 0.099989 | 0.099989 | 0.099989 | 0.099989 | Represents total cost of heat, see cell D115
Electricity for SH - Flexible | CCC | Widespread Engagement | 0.094594 | 0.10016 | 0.099657 | 0.098661 | 0.097723 | 0.096776 | 0.095838 | 0.09442 | 0.093649 | 0.092227 | 0.090779 | 0.089401 | 0.092265 | 0.092686 | 0.093111 | 0.093528 | 0.09395 | 0.091858 | 0.089846 | 0.087905 | 0.08603 | 0.084213 | 0.08245 | 0.080735 | 0.079065 | 0.077435 | 0.075843 | 0.074285 | 0.072759 | 0.071262 | 0.069793 | 0.068348 | 0.068348 | 0.068348 | 0.068348 | 0.068348 | 0.068348 | 0.068348 | 0.068348 | 0.068348 | 0.068348 | 0.068348
Electricity for SH - Inflexible | CCC | Widespread Engagement | 0.11393 | 0.11727 | 0.11697 | 0.11637 | 0.11581 | 0.11524 | 0.11468 | 0.11403 | 0.11378 | 0.11313 | 0.11246 | 0.11184 | 0.11386 | 0.11442 | 0.11498 | 0.11554 | 0.1161 | 0.11517 | 0.11429 | 0.11346 | 0.11266 | 0.1119 | 0.11117 | 0.11047 | 0.1098 | 0.10915 | 0.10852 | 0.10792 | 0.10733 | 0.10676 | 0.10621 | 0.10567 | 0.10567 | 0.10567 | 0.10567 | 0.10567 | 0.10567 | 0.10567 | 0.10567 | 0.10567 | 0.10567 | 0.10567
Electricity for SH - Highly flexible | CCC | Widespread Engagement | 0.093479 | 0.093238 | 0.091449 | 0.089808 | 0.088225 | 0.086634 | 0.08505 | 0.084209 | 0.083367 | 0.082525 | 0.081683 | 0.080842 | 0.08 | 0.079158 | 0.078316 | 0.077475 | 0.076633 | 0.075791 | 0.074949 | 0.074107 | 0.073266 | 0.072424 | 0.071582 | 0.07074 | 0.069899 | 0.069057 | 0.068215 | 0.067373 | 0.066532 | 0.06569 | 0.064848 | 0.064006 | 0.064006 | 0.064006 | 0.064006 | 0.064006 | 0.064006 | 0.064006 | 0.064006 | 0.064006 | 0.064006 | 0.064006
Electricity for HW - with storage | CCC | Widespread Engagement | 0.094594 | 0.10016 | 0.099657 | 0.098661 | 0.097723 | 0.096776 | 0.095838 | 0.09442 | 0.093649 | 0.092227 | 0.090779 | 0.089401 | 0.092265 | 0.092686 | 0.093111 | 0.093528 | 0.09395 | 0.091858 | 0.089846 | 0.087905 | 0.08603 | 0.084213 | 0.08245 | 0.080735 | 0.079065 | 0.077435 | 0.075843 | 0.074285 | 0.072759 | 0.071262 | 0.069793 | 0.068348 | 0.068348 | 0.068348 | 0.068348 | 0.068348 | 0.068348 | 0.068348 | 0.068348 | 0.068348 | 0.068348 | 0.068348
Electricity for HW - without storage | CCC | Widespread Engagement | 0.13639 | 0.1375 | 0.1374 | 0.1372 | 0.13701 | 0.13682 | 0.13664 | 0.13642 | 0.13633 | 0.13612 | 0.1359 | 0.13569 | 0.13636 | 0.13655 | 0.13674 | 0.13692 | 0.13711 | 0.1368 | 0.13651 | 0.13623 | 0.13596 | 0.13571 | 0.13547 | 0.13523 | 0.13501 | 0.13479 | 0.13458 | 0.13438 | 0.13419 | 0.134 | 0.13381 | 0.13363 | 0.13363 | 0.13363 | 0.13363 | 0.13363 | 0.13363 | 0.13363 | 0.13363 | 0.13363 | 0.13363 | 0.13363
Hydrogen | CCC | Widespread Engagement | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.1281 | 0.12122 | 0.1145 | 0.10794 | 0.10154 | 0.10113 | 0.10071 | 0.1003 | 0.099882 | 0.099467 | 0.099052 | 0.098638 | 0.098223 | 0.097808 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | 0.097394 | Residential
Heat networks - electricity-based | CCC | Widespread Engagement | 0.11589 | 0.11589 | 0.10777 | 0.099993 | 0.092213 | 0.084434 | 0.075297 | 0.075138 | 0.074979 | 0.074821 | 0.074662 | 0.072976 | 0.074803 | 0.076629 | 0.078455 | 0.080282 | 0.081758 | 0.082686 | 0.083614 | 0.084541 | 0.085469 | 0.085873 | 0.085388 | 0.084903 | 0.084418 | 0.083932 | 0.082916 | 0.082981 | 0.083045 | 0.08311 | 0.083174 | 0.082657 | 0.082657 | 0.082657 | 0.082657 | 0.082657 | 0.082657 | 0.082657 | 0.082657 | 0.082657 | 0.082657 | 0.082657 | Represents total cost of heat, see cell D115
Electricity for SH - Flexible | CCC | Widespread Innovation | 0.094594 | 0.10016 | 0.099657 | 0.098661 | 0.097723 | 0.096776 | 0.095838 | 0.09442 | 0.093649 | 0.092227 | 0.090779 | 0.089401 | 0.092283 | 0.092725 | 0.093172 | 0.093611 | 0.094056 | 0.09053 | 0.087085 | 0.083712 | 0.080405 | 0.077156 | 0.073961 | 0.070815 | 0.067714 | 0.064654 | 0.061632 | 0.058644 | 0.055688 | 0.052762 | 0.049863 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699
Electricity for SH - Inflexible | CCC | Widespread Innovation | 0.11393 | 0.11727 | 0.11697 | 0.11637 | 0.11581 | 0.11524 | 0.11468 | 0.11403 | 0.11378 | 0.11313 | 0.11246 | 0.11184 | 0.11387 | 0.11444 | 0.11502 | 0.11559 | 0.11616 | 0.11437 | 0.11264 | 0.11094 | 0.10929 | 0.10767 | 0.10608 | 0.10452 | 0.10299 | 0.10148 | 0.099997 | 0.098534 | 0.097089 | 0.095663 | 0.094253 | 0.092858 | 0.092858 | 0.092858 | 0.092858 | 0.092858 | 0.092858 | 0.092858 | 0.092858 | 0.092858 | 0.092858 | 0.092858
Electricity for SH - Highly flexible | CCC | Widespread Innovation | 0.093479 | 0.093238 | 0.091449 | 0.089808 | 0.088225 | 0.086634 | 0.08505 | 0.08345 | 0.08185 | 0.080249 | 0.078649 | 0.077049 | 0.075448 | 0.073848 | 0.072247 | 0.070647 | 0.069047 | 0.067446 | 0.065846 | 0.064246 | 0.062645 | 0.061045 | 0.059444 | 0.057844 | 0.056244 | 0.054643 | 0.053043 | 0.051443 | 0.049842 | 0.048242 | 0.046641 | 0.045041 | 0.045041 | 0.045041 | 0.045041 | 0.045041 | 0.045041 | 0.045041 | 0.045041 | 0.045041 | 0.045041 | 0.045041
Electricity for HW - with storage | CCC | Widespread Innovation | 0.094594 | 0.10016 | 0.099657 | 0.098661 | 0.097723 | 0.096776 | 0.095838 | 0.09442 | 0.093649 | 0.092227 | 0.090779 | 0.089401 | 0.092283 | 0.092725 | 0.093172 | 0.093611 | 0.094056 | 0.09053 | 0.087085 | 0.083712 | 0.080405 | 0.077156 | 0.073961 | 0.070815 | 0.067714 | 0.064654 | 0.061632 | 0.058644 | 0.055688 | 0.052762 | 0.049863 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699
Electricity for HW - without storage | CCC | Widespread Innovation | 0.13639 | 0.1375 | 0.1374 | 0.1372 | 0.13701 | 0.13682 | 0.13664 | 0.13642 | 0.13633 | 0.13612 | 0.1359 | 0.13569 | 0.13637 | 0.13656 | 0.13675 | 0.13694 | 0.13713 | 0.13653 | 0.13595 | 0.13539 | 0.13484 | 0.1343 | 0.13377 | 0.13325 | 0.13274 | 0.13224 | 0.13174 | 0.13125 | 0.13077 | 0.1303 | 0.12983 | 0.12936 | 0.12936 | 0.12936 | 0.12936 | 0.12936 | 0.12936 | 0.12936 | 0.12936 | 0.12936 | 0.12936 | 0.12936
Hydrogen | CCC | Widespread Innovation | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.090147 | 0.087562 | 0.085147 | 0.082902 | 0.080828 | 0.080022 | 0.079217 | 0.078412 | 0.077607 | 0.076802 | 0.075997 | 0.075191 | 0.074386 | 0.073581 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776
Heat networks - electricity-based | CCC | Widespread Innovation | 0.11589 | 0.11589 | 0.10777 | 0.099993 | 0.092213 | 0.084434 | 0.075297 | 0.075105 | 0.074914 | 0.074723 | 0.074531 | 0.072753 | 0.074543 | 0.076333 | 0.078123 | 0.079913 | 0.081319 | 0.081885 | 0.082451 | 0.083017 | 0.083583 | 0.083108 | 0.082256 | 0.081405 | 0.080553 | 0.079702 | 0.077671 | 0.077381 | 0.077092 | 0.076802 | 0.076513 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | Represents total cost of heat, see cell D115
Electricity for SH - Flexible | CCC | Tailwinds | 0.094594 | 0.10016 | 0.099657 | 0.098661 | 0.097723 | 0.096776 | 0.095838 | 0.09442 | 0.093649 | 0.092227 | 0.090779 | 0.089401 | 0.092283 | 0.092725 | 0.093172 | 0.093611 | 0.094056 | 0.09053 | 0.087085 | 0.083712 | 0.080405 | 0.077156 | 0.073961 | 0.070815 | 0.067714 | 0.064654 | 0.061632 | 0.058644 | 0.055688 | 0.052762 | 0.049863 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699
Electricity for SH - Inflexible | CCC | Tailwinds | 0.11393 | 0.11727 | 0.11697 | 0.11637 | 0.11581 | 0.11524 | 0.11468 | 0.11403 | 0.11378 | 0.11313 | 0.11246 | 0.11184 | 0.11387 | 0.11444 | 0.11502 | 0.11559 | 0.11616 | 0.11437 | 0.11264 | 0.11094 | 0.10929 | 0.10767 | 0.10608 | 0.10452 | 0.10299 | 0.10148 | 0.099997 | 0.098534 | 0.097089 | 0.095663 | 0.094253 | 0.092858 | 0.092858 | 0.092858 | 0.092858 | 0.092858 | 0.092858 | 0.092858 | 0.092858 | 0.092858 | 0.092858 | 0.092858
Electricity for SH - Highly flexible | CCC | Tailwinds | 0.093479 | 0.093238 | 0.091449 | 0.089808 | 0.088225 | 0.086634 | 0.08505 | 0.08345 | 0.08185 | 0.080249 | 0.078649 | 0.077049 | 0.075448 | 0.073848 | 0.072247 | 0.070647 | 0.069047 | 0.067446 | 0.065846 | 0.064246 | 0.062645 | 0.061045 | 0.059444 | 0.057844 | 0.056244 | 0.054643 | 0.053043 | 0.051443 | 0.049842 | 0.048242 | 0.046641 | 0.045041 | 0.045041 | 0.045041 | 0.045041 | 0.045041 | 0.045041 | 0.045041 | 0.045041 | 0.045041 | 0.045041 | 0.045041
Electricity for HW - with storage | CCC | Tailwinds | 0.094594 | 0.10016 | 0.099657 | 0.098661 | 0.097723 | 0.096776 | 0.095838 | 0.09442 | 0.093649 | 0.092227 | 0.090779 | 0.089401 | 0.092283 | 0.092725 | 0.093172 | 0.093611 | 0.094056 | 0.09053 | 0.087085 | 0.083712 | 0.080405 | 0.077156 | 0.073961 | 0.070815 | 0.067714 | 0.064654 | 0.061632 | 0.058644 | 0.055688 | 0.052762 | 0.049863 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699 | 0.04699
Electricity for HW - without storage | CCC | Tailwinds | 0.13639 | 0.1375 | 0.1374 | 0.1372 | 0.13701 | 0.13682 | 0.13664 | 0.13642 | 0.13633 | 0.13612 | 0.1359 | 0.13569 | 0.13637 | 0.13656 | 0.13675 | 0.13694 | 0.13713 | 0.13653 | 0.13595 | 0.13539 | 0.13484 | 0.1343 | 0.13377 | 0.13325 | 0.13274 | 0.13224 | 0.13174 | 0.13125 | 0.13077 | 0.1303 | 0.12983 | 0.12936 | 0.12936 | 0.12936 | 0.12936 | 0.12936 | 0.12936 | 0.12936 | 0.12936 | 0.12936 | 0.12936 | 0.12936
Hydrogen | CCC | Tailwinds | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.13408 | 0.090147 | 0.087562 | 0.085147 | 0.082902 | 0.080828 | 0.080022 | 0.079217 | 0.078412 | 0.077607 | 0.076802 | 0.075997 | 0.075191 | 0.074386 | 0.073581 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776 | 0.072776
Heat networks - electricity-based | CCC | Tailwinds | 0.11589 | 0.11589 | 0.10777 | 0.099993 | 0.092213 | 0.084434 | 0.075297 | 0.075105 | 0.074914 | 0.074723 | 0.074531 | 0.072753 | 0.074543 | 0.076333 | 0.078123 | 0.079913 | 0.081319 | 0.081885 | 0.082451 | 0.083017 | 0.083583 | 0.083108 | 0.082256 | 0.081405 | 0.080553 | 0.079702 | 0.077671 | 0.077381 | 0.077092 | 0.076802 | 0.076513 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | 0.07491 | Represents total cost of heat, see cell D115
Gas | CCC | All scenarios | 0.014195 | 0.017951 | 0.01868 | 0.019273 | 0.019878 | 0.020457 | 0.021037 | 0.021643 | 0.022588 | 0.023195 | 0.023778 | 0.024384 | 0.024693 | 0.025001 | 0.025309 | 0.025618 | 0.025926 | 0.025875 | 0.025823 | 0.025772 | 0.025721 | 0.02567 | 0.025618 | 0.025567 | 0.025516 | 0.025464 | 0.025413 | 0.025362 | 0.025311 | 0.025259 | 0.025208 | 0.025157 | 0.025157 | 0.025157 | 0.025157 | 0.025157 | 0.025157 | 0.025157 | 0.025157 | 0.025157 | 0.025157 | 0.025157 | Residential
Biomass | CCC | All scenarios | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968 | 0.021968
Oil | CCC | All scenarios | 0.034886 | 0.031031 | 0.031633 | 0.03221 | 0.033745 | 0.03475 | 0.035753 | 0.036707 | 0.037707 | 0.039229 | 0.040177 | 0.041172 | 0.042214 | 0.043256 | 0.04482 | 0.045862 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | 0.046905 | Burning oil; data from CCC using a kWh/L conversion of 10.2704459499627
Solid | CCC | All scenarios | 0.0092988 | 0.0089164 | 0.008787 | 0.0086738 | 0.0085743 | 0.0085743 | 0.0085743 | 0.0085743 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | 0.0086577 | Only used to derive 'Other'
Other | CCC | All scenarios | 0.026514 | 0.024741 | 0.024999 | 0.025247 | 0.025928 | 0.02638 | 0.026832 | 0.027261 | 0.027719 | 0.028404 | 0.028831 | 0.029279 | 0.029748 | 0.030217 | 0.03092 | 0.031389 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 0.031858 | 45% oil, 45% biomass, 10% solid
BioLPG | CCC | All scenarios | 0.07239 | 0.071811 | 0.071232 | 0.070654 | 0.070075 | 0.069496 | 0.068917 | 0.068338 | 0.06776 | 0.067181 | 0.066602 | 0.066023 | 0.066679 | 0.066822 | 0.070133 | 0.072208 | 0.073547 | 0.074405 | 0.074936 | 0.075234 | 0.075362 | 0.075359 | 0.074816 | 0.074267 | 0.073717 | 0.073165 | 0.072609 | 0.072053 | 0.071493 | 0.070933 | 0.07037 | 0.069806 | 0.069806 | 0.069806 | 0.069806 | 0.069806 | 0.069806 | 0.069806 | 0.069806 | 0.069806 | 0.069806 | 0.069806
CO2 intensity (kgCO2/kWh or kgCO2e/kWh) Direct and indirect emissions. N.B. Where indirect emissions, presented as CO2e, with CH4 and N2O not separated out below. Where direct emissions, presented as CO2, with CH4 and N2O separated out below.
Fuel type | Source | Scenario | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | Comments
Electricity for SH - Flexible | CCC | All scenarios | 0.19569 | 0.18244 | 0.1692 | 0.15595 | 0.14271 | 0.12946 | 0.11622 | 0.10298 | 0.089732 | 0.076488 | 0.063244 | 0.05 | 0.04772 | 0.045441 | 0.043161 | 0.040882 | 0.038602 | 0.036322 | 0.034043 | 0.031763 | 0.029484 | 0.027204 | 0.024924 | 0.022645 | 0.020365 | 0.018086 | 0.015806 | 0.013527 | 0.011247 | 0.0089673 | 0.0066877 | 0.0044081 | 0.0044081 | 0.0044081 | 0.0044081 | 0.0044081 | 0.0044081 | 0.0044081 | 0.0044081 | 0.0044081 | 0.0044081 | 0.0044081 | kgCO2e, Indirect emissions
Electricity for SH - Inflexible | CCC | All scenarios | 0.37335 | 0.35502 | 0.3367 | 0.31837 | 0.30005 | 0.28172 | 0.26339 | 0.24507 | 0.22674 | 0.20841 | 0.19009 | 0.17176 | 0.16396 | 0.15617 | 0.14837 | 0.14057 | 0.13277 | 0.12497 | 0.11718 | 0.10938 | 0.10158 | 0.093781 | 0.085983 | 0.078185 | 0.070387 | 0.062588 | 0.05479 | 0.046992 | 0.039194 | 0.031396 | 0.023598 | 0.015799 | 0.015799 | 0.015799 | 0.015799 | 0.015799 | 0.015799 | 0.015799 | 0.015799 | 0.015799 | 0.015799 | 0.015799 | kgCO2e, Indirect emissions
Electricity for SH - Highly flexible | CCC | All scenarios | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | kgCO2e, Indirect emissions
Electricity for HW - with storage | CCC | All scenarios | 0.15655 | 0.14595 | 0.13536 | 0.12476 | 0.11417 | 0.10357 | 0.092977 | 0.082381 | 0.071786 | 0.061191 | 0.050595 | 0.04 | 0.038176 | 0.036353 | 0.034529 | 0.032705 | 0.030882 | 0.029058 | 0.027234 | 0.025411 | 0.023587 | 0.021763 | 0.01994 | 0.018116 | 0.016292 | 0.014469 | 0.012645 | 0.010821 | 0.0089975 | 0.0071739 | 0.0053502 | 0.0035265 | 0.0035265 | 0.0035265 | 0.0035265 | 0.0035265 | 0.0035265 | 0.0035265 | 0.0035265 | 0.0035265 | 0.0035265 | 0.0035265 | kgCO2e, Indirect emissions
Electricity for HW - without storage | CCC | All scenarios | 0.55102 | 0.52761 | 0.5042 | 0.48079 | 0.45738 | 0.43397 | 0.41057 | 0.38716 | 0.36375 | 0.34034 | 0.31693 | 0.29352 | 0.28021 | 0.26689 | 0.25357 | 0.24026 | 0.22694 | 0.21362 | 0.20031 | 0.18699 | 0.17367 | 0.16036 | 0.14704 | 0.13372 | 0.12041 | 0.10709 | 0.093774 | 0.080458 | 0.067141 | 0.053824 | 0.040507 | 0.027191 | 0.027191 | 0.027191 | 0.027191 | 0.027191 | 0.027191 | 0.027191 | 0.027191 | 0.027191 | 0.027191 | 0.027191 | kgCO2e, Indirect emissions
Gas | CCC | All scenarios | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | 0.18351 | kgCO2, Direct emissions
Biomass | CCC | All scenarios | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | kgCO2, Direct emissions, as used in cost optimised modelling (£/t reporting based on full lifecycle emissions, including indirect emissions)
Oil | CCC | All scenarios | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | 0.24553 | kgCO2, Direct emissions
Solid | CCC | All scenarios | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | 0.32835 | kgCO2, Direct emissions
Other | CCC | All scenarios | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | 0.12183 | kgCO2, Direct emissions. Blended fuel composed of 45% oil, 45% biomass, 10% solid
BioLPG | CCC | All scenarios | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | kgCO2, Direct emissions, as used in cost optimised modelling (£/t reporting based on full lifecycle emissions, including indirect emissions)
Hydrogen | CCC | Balanced Net Zero Pathway | 0.29207 | 0.2723 | 0.25253 | 0.23277 | 0.213 | 0.19323 | 0.17346 | 0.12918 | 0.092045 | 0.061918 | 0.038655 | 0.022117 | 0.021501 | 0.020892 | 0.020292 | 0.0197 | 0.019116 | 0.018539 | 0.017969 | 0.017407 | 0.016852 | 0.015662 | 0.015156 | 0.014649 | 0.014143 | 0.013636 | 0.01313 | 0.012623 | 0.012117 | 0.01161 | 0.011104 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | kgCO2, Indirect emissions. Indirect CH4 and N2O emissions not accounted for, leading to a slight underestimate
Heat networks - electricity-based | CCC | Balanced Net Zero Pathway | 0.0077948 | 0.0077948 | 0.0072538 | 0.0067128 | 0.0061718 | 0.0056308 | 0.0050898 | 0.0045307 | 0.0039717 | 0.0034126 | 0.0028536 | 0.0022945 | 0.0022073 | 0.0021201 | 0.002033 | 0.0019458 | 0.0018586 | 0.0017605 | 0.0016623 | 0.0015642 | 0.0014661 | 0.001368 | 0.0012588 | 0.0011497 | 0.0010406 | 0.00093143 | 0.00082229 | 0.00070442 | 0.00058654 | 0.00046867 | 0.00035079 | 0.00023291 | 0.00023291 | 0.00023291 | 0.00023291 | 0.00023291 | 0.00023291 | 0.00023291 | 0.00023291 | 0.00023291 | 0.00023291 | 0.00023291 | kgCO2e, Indirect emissions
Hydrogen | CCC | Headwinds | 0.29207 | 0.2723 | 0.25253 | 0.23277 | 0.213 | 0.19323 | 0.17346 | 0.12918 | 0.092045 | 0.061918 | 0.038655 | 0.022117 | 0.021501 | 0.020892 | 0.020292 | 0.0197 | 0.019116 | 0.018539 | 0.017969 | 0.017407 | 0.016852 | 0.015662 | 0.015156 | 0.014649 | 0.014143 | 0.013636 | 0.01313 | 0.012623 | 0.012117 | 0.01161 | 0.011104 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | kgCO2, Indirect emissions. Indirect CH4 and N2O emissions not accounted for, leading to a slight underestimate
Hydrogen - High | CCC | Headwinds | 0.29207 | 0.2723 | 0.25253 | 0.23277 | 0.213 | 0.19323 | 0.17346 | 0.12918 | 0.092045 | 0.061918 | 0.038655 | 0.022117 | 0.021501 | 0.020892 | 0.020292 | 0.0197 | 0.019116 | 0.018539 | 0.017969 | 0.017407 | 0.016852 | 0.015662 | 0.015156 | 0.014649 | 0.014143 | 0.013636 | 0.01313 | 0.012623 | 0.012117 | 0.01161 | 0.011104 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | kgCO2, Indirect emissions. Indirect CH4 and N2O emissions not accounted for, leading to a slight underestimate
Hydrogen - Low | CCC | Headwinds | 0.29207 | 0.2723 | 0.25253 | 0.23277 | 0.213 | 0.19323 | 0.17346 | 0.12918 | 0.092045 | 0.061918 | 0.038655 | 0.022117 | 0.021501 | 0.020892 | 0.020292 | 0.0197 | 0.019116 | 0.018539 | 0.017969 | 0.017407 | 0.016852 | 0.015662 | 0.015156 | 0.014649 | 0.014143 | 0.013636 | 0.01313 | 0.012623 | 0.012117 | 0.01161 | 0.011104 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | 0.010597 | kgCO2, Indirect emissions. Indirect CH4 and N2O emissions not accounted for, leading to a slight underestimate
Heat networks - gas to hydrogen peaking | CCC | Headwinds | 0.053562 | 0.053562 | 0.052597 | 0.051632 | 0.050668 | 0.049703 | 0.048738 | 0.048167 | 0.047596 | 0.047025 | 0.046453 | 0.045882 | 0.044352 | 0.042823 | 0.041293 | 0.039763 | 0.037751 | 0.036487 | 0.034638 | 0.033011 | 0.029735 | 0.024745 | 0.018799 | 0.013536 | 0.010235 | 0.0070909 | 0.0059033 | 0.0047128 | 0.0031205 | 0.0018387 | 0.00013299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | kgCO2, Direct emissions
Heat networks - gas to hydrogen peaking | CCC | Headwinds | 0.0051889 | 0.0051889 | 0.004867 | 0.0045451 | 0.0042231 | 0.0039012 | 0.0035792 | 0.0031999 | 0.0028207 | 0.0024414 | 0.0020621 | 0.0016828 | 0.0016392 | 0.0015956 | 0.0015521 | 0.0015085 | 0.0015152 | 0.001629 | 0.0017839 | 0.0018996 | 0.0021456 | 0.0025109 | 0.0029461 | 0.0032893 | 0.0034505 | 0.0035811 | 0.0035547 | 0.0034811 | 0.0034265 | 0.0033431 | 0.0032782 | 0.0031136 | 0.0031136 | 0.0031136 | 0.0031136 | 0.0031136 | 0.0031136 | 0.0031136 | 0.0031136 | 0.0031136 | 0.0031136 | 0.0031136 | kgCO2e, Indirect emissions. Indirect CH4 and N2O hydrogen emissions not accounted for, leading to a slight underestimate
Hydrogen | CCC | Widespread Engagement | 0.29207 | 0.2723 | 0.25253 | 0.23277 | 0.213 | 0.19323 | 0.17346 | 0.13798 | 0.1069 | 0.080119 | 0.057557 | 0.039127 | 0.037253 | 0.035404 | 0.033579 | 0.031778 | 0.030001 | 0.028247 | 0.026515 | 0.024805 | 0.023117 | 0.021259 | 0.019718 | 0.018178 | 0.016638 | 0.015098 | 0.013557 | 0.012017 | 0.010477 | 0.0089366 | 0.0073963 | 0.005856 | 0.005856 | 0.005856 | 0.005856 | 0.005856 | 0.005856 | 0.005856 | 0.005856 | 0.005856 | 0.005856 | 0.005856 | kgCO2, Indirect emissions. Indirect CH4 and N2O emissions not accounted for, leading to a slight underestimate
Heat networks - electricity-based | CCC | Widespread Engagement | 0.0079988 | 0.0079988 | 0.0074437 | 0.0068885 | 0.0063333 | 0.0057782 | 0.005223 | 0.0046493 | 0.0040756 | 0.003502 | 0.0029283 | 0.0023546 | 0.0022651 | 0.0021756 | 0.0020862 | 0.0019967 | 0.0019072 | 0.0018065 | 0.0017058 | 0.0016051 | 0.0015045 | 0.0014038 | 0.0012918 | 0.0011798 | 0.0010678 | 0.00095581 | 0.00084382 | 0.00072286 | 0.00060189 | 0.00048093 | 0.00035997 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | kgCO2e, Indirect emissions
Hydrogen | CCC | Widespread Innovation | 0.29207 | 0.2723 | 0.25253 | 0.23277 | 0.213 | 0.19323 | 0.17346 | 0.14219 | 0.11409 | 0.089078 | 0.067104 | 0.048103 | 0.045667 | 0.043263 | 0.040891 | 0.038549 | 0.036239 | 0.033958 | 0.031707 | 0.029484 | 0.02729 | 0.025046 | 0.023044 | 0.021042 | 0.019039 | 0.017037 | 0.015035 | 0.013032 | 0.01103 | 0.0090277 | 0.0070254 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | kgCO2, Indirect emissions. Indirect CH4 and N2O emissions not accounted for, leading to a slight underestimate
Heat networks - electricity-based | CCC | Widespread Innovation | 0.0079988 | 0.0079988 | 0.0074437 | 0.0068885 | 0.0063333 | 0.0057782 | 0.005223 | 0.0046493 | 0.0040756 | 0.003502 | 0.0029283 | 0.0023546 | 0.0022651 | 0.0021756 | 0.0020862 | 0.0019967 | 0.0019072 | 0.0018065 | 0.0017058 | 0.0016051 | 0.0015045 | 0.0014038 | 0.0012918 | 0.0011798 | 0.0010678 | 0.00095581 | 0.00084382 | 0.00072286 | 0.00060189 | 0.00048093 | 0.00035997 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | kgCO2e, Indirect emissions
Hydrogen | CCC | Tailwinds | 0.29207 | 0.2723 | 0.25253 | 0.23277 | 0.213 | 0.19323 | 0.17346 | 0.14219 | 0.11409 | 0.089078 | 0.067104 | 0.048103 | 0.045667 | 0.043263 | 0.040891 | 0.038549 | 0.036239 | 0.033958 | 0.031707 | 0.029484 | 0.02729 | 0.025046 | 0.023044 | 0.021042 | 0.019039 | 0.017037 | 0.015035 | 0.013032 | 0.01103 | 0.0090277 | 0.0070254 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | 0.005023 | kgCO2, Indirect emissions. Indirect CH4 and N2O emissions not accounted for, leading to a slight underestimate
Heat networks - electricity-based | CCC | Tailwinds | 0.0079988 | 0.0079988 | 0.0074437 | 0.0068885 | 0.0063333 | 0.0057782 | 0.005223 | 0.0046493 | 0.0040756 | 0.003502 | 0.0029283 | 0.0023546 | 0.0022651 | 0.0021756 | 0.0020862 | 0.0019967 | 0.0019072 | 0.0018065 | 0.0017058 | 0.0016051 | 0.0015045 | 0.0014038 | 0.0012918 | 0.0011798 | 0.0010678 | 0.00095581 | 0.00084382 | 0.00072286 | 0.00060189 | 0.00048093 | 0.00035997 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | 0.00023901 | kgCO2e, Indirect emissions
CH4 intensity (kgCO2e/kWh), direct emissions only.
Fuel type | Source | Scenario | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | Comments
Heat networks - gas to hydrogen peaking | CCC | Headwinds | 9.5267e-05 | 9.5267e-05 | 9.3552e-05 | 9.1836e-05 | 9.012e-05 | 8.8404e-05 | 8.6688e-05 | 8.5672e-05 | 8.4656e-05 | 8.364e-05 | 8.2624e-05 | 8.1608e-05 | 7.8888e-05 | 7.6167e-05 | 7.3446e-05 | 7.0725e-05 | 6.7146e-05 | 6.4898e-05 | 6.1609e-05 | 5.8715e-05 | 5.2888e-05 | 4.4012e-05 | 3.3437e-05 | 2.4075e-05 | 1.8204e-05 | 1.2612e-05 | 1.05e-05 | 8.3824e-06 | 5.5502e-06 | 3.2704e-06 | 2.3654e-07 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Biomass | CCC | All scenarios | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | 0.033836 | As used in cost optimised modelling (£/t reporting based on full lifecycle emissions, including indirect emissions)
Gas | CCC | All scenarios | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264 | 0.0003264
Oil | CCC | All scenarios | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296 | 0.0008296
Solid | CCC | All scenarios | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | 0.0012648 | Industrial
Other | CCC | All scenarios | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 0.0020224 | 45% oil, 45% biomass, 10% solid
BioLPG | CCC | All scenarios | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | 0.00019268 | As used in cost optimised modelling (£/t reporting based on full lifecycle emissions, including indirect emissions)
N2O intensity (kgCO2e/kWh), direct emissions only.
Fuel type | Source | Scenario | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | Comments
Heat networks - gas to hydrogen peaking | CCC | Headwinds | 2.9187e-05 | 2.9187e-05 | 2.8662e-05 | 2.8136e-05 | 2.761e-05 | 2.7085e-05 | 2.6559e-05 | 2.6248e-05 | 2.5936e-05 | 2.5625e-05 | 2.5314e-05 | 2.5003e-05 | 2.4169e-05 | 2.3335e-05 | 2.2502e-05 | 2.1668e-05 | 2.0572e-05 | 1.9883e-05 | 1.8875e-05 | 1.7989e-05 | 1.6203e-05 | 1.3484e-05 | 1.0244e-05 | 7.376e-06 | 5.5773e-06 | 3.864e-06 | 3.2169e-06 | 2.5681e-06 | 1.7004e-06 | 1.002e-06 | 7.2469e-08 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Biomass | CCC | All scenarios | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | 0.0039542 | As used in cost optimised modelling (£/t reporting based on full lifecycle emissions, including indirect emissions)
Gas | CCC | All scenarios | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001 | 0.0001
Oil | CCC | All scenarios | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061 | 0.00061
Solid | CCC | All scenarios | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | 0.00256 | Industrial
Other | CCC | All scenarios | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 0.0023099 | 45% oil, 45% biomass, 10% solid
BioLPG | CCC | All scenarios | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | 0.00013949 | As used in cost optimised modelling (£/t reporting based on full lifecycle emissions, including indirect emissions)
Assumptions and sources
Fuel type | Source | [11 empty] | Assumptions
Electricity for SH - Flexible | CCC assumptions | [11 empty] | Value flat after 2050
Electricity for SH - Inflexible | CCC assumptions | [11 empty] | Value flat after 2050
Electricity for SH - Highly flexible | CCC assumptions | [11 empty] | Value flat after 2050
Electricity for HW - with storage | CCC assumptions | [11 empty] | Value flat after 2050
Electricity for HW - without storage | CCC assumptions | [11 empty] | Value flat after 2050
Gas | CCC assumptions | [11 empty] | Value flat after 2050; residential
Hydrogen | CCC assumptions | [11 empty] | Value flat after 2050; residential. Indirect emissions from CH4 and N2O not accounted for, leading to a slight underestimate in the reported total indirect emissions.
Biomass | CCC assumptions | [11 empty] | Value flat after 2050
Oil | CCC assumptions | [11 empty] | Value flat after 2050; burning oil - data from CCC using a kWh/L conversion of 10.2704459499627
BioLPG | CCC assumptions | [11 empty] | Value flat after 2050; this fuel type was used as a proxy as part of an illustrative biofuel system.
Solid | CCC assumptions | [11 empty] | Value flat after 2050
Gas & Oil emissions | CCC assumptions
Heat from low carbon heat networks | Cost and CO2 emissions calculated from modelling results based on District heating and local approaches to heat decarbonisation (2015) Element Energy for CCC. Costs represent an updated calculation considering the total cost of heat, including non-network capex, network capex, opex and fuel costs in addition to separated lifetimes for the non-network and network components. For the purposes or reporting, capex components of fuel costs were reallocated from reported operational costs to reported investment costs. | [11 empty] | Commercial hydrogen prices and emissions used where relevant. Indirect CH4 and N2O emissions from hydrogen are not accounted for, leading to a slight underestimate in the reported total indirect emissions.

## Measures and costs
Standard Costs
Final Costs in £ material + labour; * denotes additional uncertainty over scope of costs
|  | Flat CNV |  |  | Flat LR |  |  | Flat HR |  |  | Mid Terrace |  |  | End Terrace |  |  | Semi Detached |  |  | Detached |  |  | Bungalow |  |  | Final Price Year | Sources | Main source of data analysis | Adjustment incorprating case study data | Hard-to-Treat (HTT) assumptions
| Measures/ size | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L | 2019 | Main Sources of data
1 | Solid wall insulation (External)* | 4453.8706 | 6362.6723 | 8271.474 | 4453.8706 | 6362.6723 | 8271.474 | 4453.8706 | 6362.6723 | 8271.474 | 5307.5292 | 7582.1845 | 9856.8399 | 6899.7879 | 9856.8399 | 12813.8918 | 6012.7253 | 8589.6076 | 11166.4899 | 8054.0827 | 11505.8324 | 14957.5822 | 7274.6554 | 10392.3648 | 13510.0742 | Converted from 2016 prices | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. | University College London (UCL), 2020. Analysis Work to Refine Fabric Energy Efficiency Assumptions for use in Developing the Sixth Carbon Budget. | Non-BEIS/CAR data low uncertainty | HTT costs provided by UCL were subsequently disaggregated by the CCC for use in modelling. The HTT costs in this table represent a subset of non-standard wall and roof types which fall in our definition of economic potential. For example, this includes cavities in concrete dwellings, walls with conservatories, narrow cavities, high walls, and standard lofts with access issues only. Other categories are also excluded from our economic potential in this work.
2 | Solid wall insulation (Internal)* | 2338.2821 | 3340.403 | 4342.5239 | 2338.2821 | 3340.403 | 4342.5239 | 2338.2821 | 3340.403 | 4342.5239 | 2857.9003 | 4082.7147 | 5307.5292 | 3715.2704 | 5307.5292 | 6899.7879 | 5121.9512 | 7317.0732 | 9512.1951 | 6161.1877 | 8801.6967 | 11442.2057 | 4676.5642 | 6680.8059 | 8685.0477 | Converted from 2016 prices | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. |  | Non-BEIS/CAR data low uncertainty
3 | Solid Wall insulation (Thin)* | 1683.9873 | 2405.0901 | 3126.6172 | 1683.9873 | 2405.0901 | 3126.3081 | 1683.9873 | 2405.0901 | 3126.6172 | 2057.6882 | 2939.5546 | 3821.421 | 2674.9947 | 3821.421 | 4967.8473 | 3687.8049 | 5268.2927 | 6848.7805 | 4436.0551 | 6337.2216 | 8238.3881 | 3367.1262 | 4810.1803 | 6253.2344 | Converted from 2016 prices | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. Glew, D., Parker, D., Miles-Shenton, D., Fletcher, M., Thomas, F., Booth, J., Cobden, L. for BEIS, (Forthcoming). Thin Internal Wall Insulation (TIWI) Project. |  | N/A
4 | Easy to treat cavities (Unfilled)* | 300.6363 | 429.4804 | 558.3245 | 301.0227 | 429.4804 | 558.7109 | 300.6363 | 429.4804 | 558.3245 | 358.145 | 511.6357 | 665.1265 | 465.5885 | 665.1265 | 864.6644 | 441.2969 | 630.4242 | 819.5514 | 604.9841 | 864.263 | 1123.5419 | 482.5027 | 689.2895 | 896.0764 | Converted from 2016 prices | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. |  | Non-BEIS/CAR data low uncertainty
5 | Hard to treat cavities (Unfilled)* | 1202.8789 | 1718.3984 | 2233.9179 | 1269.1703 | 1813.1004 | 2357.0306 | 1269.1703 | 1813.1004 | 2357.0306 | 1301.7719 | 1859.6742 | 2417.5764 | 1981.27 | 2830.3857 | 3679.5014 | 1733.3765 | 2476.2522 | 3219.1279 | 3567.497 | 5096.4243 | 6625.3517 | 2675.6228 | 3822.3183 | 4969.0137 | 2019 Price year | EST, 2019. Determining the costs of insulating non-standard cavity walls and lofts. Department for Business, Energy & Industrial Strategy. |  | Non-BEIS/CAR & EST data low uncertainty & wider evidence base introducess higher degree of uncertainty
6 | Partially filled cavities | 2338.2821 | 3340.403 | 4342.5239 | 2338.2821 | 3340.403 | 4342.5239 | 2338.2821 | 3340.403 | 4342.5239 | 2857.9003 | 4082.7147 | 5307.5292 | 3715.2704 | 5307.5292 | 6899.7879 | 5121.9512 | 7317.0732 | 9512.1951 | 6161.1877 | 8801.6967 | 11442.2057 | 4676.5642 | 6680.8059 | 8685.0477 | Converted from 2016 prices | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. |  | Non-BEIS/CAR data low uncertainty & wider evidence base introducess higher degree of uncertainty
7 | Loft insulation* | 278.3669 | 397.667 | 516.9671 | 278.3669 | 397.667 | 516.9671 | 278.3669 | 397.667 | 516.9671 | 285.79 | 408.2715 | 530.7529 | 371.527 | 530.7529 | 689.9788 | 308.0594 | 440.0848 | 572.1103 | 411.983 | 588.5472 | 765.1113 | 460.2333 | 657.4761 | 854.719 | Converted from 2016 prices | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. |  | Non-BEIS/CAR data low uncertainty
8 | Loft insulation (HTT)* | 646.8 | 924 | 1201.2 | 646.8 | 924 | 1201.2 | 646.8 | 924 | 1201.2 | 427.7 | 611 | 794.3 | 427.7 | 611 | 794.3 | 516.6 | 738 | 959.4 | 903 | 1290 | 1677 | 677.25 | 967.5 | 1257.75 | 2019 Price year | EST, 2019. Determining the costs of insulating non-standard cavity walls and lofts. Department for Business, Energy & Industrial Strategy. |  | Non-BEIS/CAR data low uncertainty
9 | Suspended timber floor insulation | 2605.4544 | 3722.0777 | 4838.7011 | 2045.0206 | 2921.4581 | 3797.8955 | 2045.0206 | 2921.4581 | 3797.8955 | 1626.5469 | 2323.6384 | 3020.7299 | 1670.8079 | 2386.8685 | 3102.929 | 1796.3927 | 2566.2753 | 3336.1579 | 2769.5438 | 3956.4911 | 5143.4385 | 2871.1924 | 4101.7035 | 5332.2145 | Converted from 2016 prices | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. |  | Non-BEIS/CAR has limited data sample but in line with CS data. For 2 storey dwellings only ground floor is insulated
10 | Solid floor insulation | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 2602.475 | 3717.8214 | 4833.1679 | 3437.0906 | 3818.9895 | 4964.6864 | 2874.2283 | 4106.0405 | 5337.8526 | 4431.2701 | 6330.3858 | 8229.5015 | 4593.9079 | 6562.7256 | 8531.5433 | Converted from 2016 prices | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. Green, G., Lannon, S., Patterson, J., Iowerth, H., 2019. Homesof today for tomorrow : Decarbonising Welsh Housing between 2020 and 2050- STAGE 2: Exploring the potential of the Welsh housing stock to meet 2050 decarbonisation targets. Welsh School of Architecture, Cardiff University. Rickaby (2017) CAPITAL COSTS OF ENERGY IMPROVEMENT MEASURES.Savills |  | N/A-For 2 storey dwellings only ground floor is insulated
11 | Secondary glazing* | 2226.9353 | 3181.3362 | 4135.737 | 2226.9353 | 3181.3362 | 4135.737 | 2226.9353 | 3181.3362 | 4135.737 | 3303.2874 | 4718.982 | 6134.6766 | 4294.2736 | 6134.6766 | 7975.0795 | 4416.755 | 6309.6501 | 8202.5451 | 5270.4136 | 7529.1622 | 9787.9109 | 4899.2577 | 6998.9396 | 9098.6214 | Converted from 2016 prices | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. |  | N/A
12 | Double glazing * | 2226.9353 | 3181.3362 | 4135.737 | 2226.9353 | 3181.3362 | 4135.737 | 2226.9353 | 3181.3362 | 4135.737 | 3303.2874 | 4718.982 | 6134.6766 | 4294.2736 | 6134.6766 | 7975.0795 | 4416.755 | 6309.6501 | 8202.5451 | 5270.4136 | 7529.1622 | 9787.9109 | 4899.2577 | 6998.9396 | 9098.6214 | Converted from 2016 prices | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. |  | N/A
13 | Double Glazing- Slim profile* | 2672.3224 | 3817.6034 | 4962.8844 | 2672.3224 | 3817.6034 | 4962.8844 | 2672.3224 | 3817.6034 | 4962.8844 | 3963.9449 | 5662.7784 | 7361.6119 | 5153.1283 | 7361.6119 | 9570.0954 | 5300.106 | 7571.5801 | 9843.0541 | 6324.4963 | 9034.9947 | 11745.4931 | 5879.1092 | 8398.7275 | 10918.3457 | Converted from 2016 prices | Heath, N., Baker, P., Menzies, G., 2010. Slim‐profile double glazing: Thermal performance and embodied energy. Historic Scotland. |  | Adjust costing to 20% increase over DG costing
14 | Triple Glazing* | 2727.9958 | 3897.1368 | 5066.2778 | 2728.3821 | 3897.1368 | 5066.6642 | 2727.9958 | 3897.1368 | 5066.2778 | 4046.527 | 5780.7529 | 7514.9788 | 5260.4852 | 7514.9788 | 9769.4724 | 5410.5249 | 7729.3213 | 10048.1177 | 6456.2566 | 9223.2238 | 11990.1909 | 6001.5907 | 8573.701 | 11145.8112 | Converted from 2016 prices | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. |  | Adjust costing to 30% increase over DG costing
15 | Insulated doors | 0 | 0 | 0 | 788.6715 | 788.6715 | 788.6715 | 0 | 0 | 0 | 1082.2511 | 2164.5022 | 2164.5022 | 1082.2511 | 2164.5022 | 2164.5022 | 1082.2511 | 2164.5022 | 2164.5022 | 1082.2511 | 2164.5022 | 2164.5022 | 1082.2511 | 2164.5022 | 2164.5022 | Converted from 2015 prices | Rickaby (2017) CAPITAL COSTS OF ENERGY IMPROVEMENT MEASURES.Savills |  | N/A
16 | Draught proofing (draught stripping) | 68.929 | 68.929 | 68.929 | 68.929 | 68.929 | 68.929 | 68.929 | 68.929 | 68.929 | 143.1601 | 143.1601 | 143.1601 | 143.1601 | 143.1601 | 143.1601 | 291.6225 | 291.6225 | 291.6225 | 291.6225 | 291.6225 | 291.6225 | 143.1601 | 143.1601 | 143.1601 | Converted from 2016 prices | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. |  | Non- CS data includes non-typical measures added to range rathar than typical costs
17 | Reduced infiltration (foam, strips, sealent use) | 17.2322 | 17.2322 | 17.2322 | 17.039 | 17.039 | 17.039 | 17.2322 | 17.2322 | 17.2322 | 35.79 | 35.79 | 35.79 | 35.79 | 35.79 | 35.79 | 72.9056 | 72.9056 | 72.9056 | 72.9056 | 72.9056 | 72.9056 | 35.79 | 35.79 | 35.79 | Converted from 2016 prices | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. |  | N/A
18 | HW Tank insulation | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | 90.1379 | Converted from 2016 prices | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. |  | N/A
19 | Ventilation | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | 541.1255 | Converted from 2015 prices | Rickaby (2017) CAPITAL COSTS OF ENERGY IMPROVEMENT MEASURES.Savills |  | N/A
20.a | Internal shading (curtains/low spec)* | 0-453 | 0-453 | 0-453 | 0-453 | 0-453 | 0-453 | 0-453 | 0-453 | 0-453 | 0-630 | 0-630 | 0-630 | 0-630 | 0-630 | 0-630 | 0-680 | 0-680 | 0-680 | 0-1410 | 0-1410 | 0-1410 | N/A | N/A | N/A | 2020 prices | CCC analysis, cost data from Blinds and Shutters Association 2020 | Blinds and Shutters Association | N/A
20.b | Internal shading (high spec)* | 654-814 | 654-814 | 654-814 | 654-814 | 654-814 | 654-814 | 654-814 | 654-814 | 654-814 | 900-1100 | 900-1100 | 900-1100 | 900-1100 | 900-1100 | 900-1100 | 950-1230 | 950-1230 | 950-1230 | 2030-2510 | 2030-2510 | 2030-2510 | N/A | N/A | N/A | 2020 prices | CCC analysis, cost data from Blinds and Shutters Association 2020 |  | N/A
20.c | External shading | 2028-3500 | 2028-3500 | 2028-3500 | 2028-3500 | 2028-3500 | 2028-3500 | 2027-3500 | 2027-3500 | 2027-3500 | 2800-3950 | 2800-3840 | 2800-3950 | 2800-3950 | 2800-3950 | 2800-3950 | 2900-4070 | 2900-4070 | 2900-4070 | 2900-8950 | 2900-8950 | 2900-8950 | N/A | N/A | N/A | 2020 prices | CCC analysis, cost data from Blinds and Shutters Association 2020 |  | N/A
Uncertainty |  |  |  |  | Low |  | Medium |  | High
Supplementary Costs Items
| Cost Type | Cost Item | Unit | Average | Price Year (2019) | Source
1a | Construction Overheads - Flat LR | Scaffolding - associated with external walls (insulation) only | Fixed £/house | 668.0806 | Converted from 2016 prices | Rickaby (2017) CAPITAL COSTS OF ENERGY IMPROVEMENT MEASURES.Savills
1b | Construction Overheads - Flat HR | Scaffolding - associated with external walls (insulation) only | Fixed £/house | 1590.6681 | Converted from 2016 prices | Rickaby (2017) CAPITAL COSTS OF ENERGY IMPROVEMENT MEASURES.Savills
1c | Construction Overheads - Terrace | Scaffolding - associated with external walls (insulation) only | Fixed £/house | 827.1474 | Converted from 2016 prices | Rickaby (2017) CAPITAL COSTS OF ENERGY IMPROVEMENT MEASURES.Savills
1d | Construction Overheads - Semi Detached | Scaffolding - associated with external walls (insulation) only | Fixed £/house | 986.2142 | Converted from 2016 prices | Rickaby (2017) CAPITAL COSTS OF ENERGY IMPROVEMENT MEASURES.Savills
1e | Construction Overheads - Detached | Scaffolding - associated with external walls (insulation) only | Fixed £/house | 986.2142 | Converted from 2016 prices | Rickaby (2017) CAPITAL COSTS OF ENERGY IMPROVEMENT MEASURES.Savills
2 | Design & Plannning | Survey and Design | Fixed £/house | 1352.0679 | Converted from 2016 prices | PRP, Peabody, 2016. ETI Domestic Retrofit Demonstration Project, Summative Report 1. ETI.
Lower Bound Costs - Included where variation assumed for lower bound
Final Costs in £ material + labour, * denotes additional uncertainty over scope of costs
|  | Flat CNV |  |  | Flat LR |  |  | Flat HR |  |  | Mid Terrace |  |  | End Terrace |  |  | Semi Detached |  |  | Detached |  |  | Bungalow |  |  | Derivation | Sources | Final Price Year
| Measures/ size | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L |  | Main Sources of data | 2019
1 | Solid wall insulation (External)* | 4082.7147 | 5832.4496 | 7582.1845 | 4082.7147 | 5832.4496 | 7582.1845 | 4082.7147 | 5832.4496 | 7582.1845 | 4825.0265 | 6892.895 | 8960.7635 | 6272.5345 | 8960.7635 | 11648.9926 | 5493.1071 | 7847.2959 | 10201.4846 | 7014.8462 | 10021.2089 | 13027.5716 | 3711.5589 | 5302.2269 | 6892.895 | Based on lower bound cost in CAR (2017) | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. | Converted from 2016 prices
2 | Solid wall insulation (Internal)* | 2041.3574 | 2916.2248 | 3791.0923 | 2041.3574 | 2916.2248 | 3791.0923 | 2041.3574 | 2916.2248 | 3791.0923 | 2598.0912 | 3711.5589 | 4825.0265 | 3377.5186 | 4825.0265 | 6272.5345 | 4082.7147 | 5832.4496 | 7582.1845 | 5047.72 | 7211.0286 | 9374.3372 | 4156.9459 | 5938.4942 | 7720.0424 | Based on lower bound cost in CAR (2017) | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. | Converted from 2016 prices
3 | Solid Wall insulation (Thin)* | 1469.7773 | 2099.6819 | 2729.5864 | 1469.7773 | 2099.6819 | 2729.5864 | 1469.7773 | 2099.6819 | 2729.5864 | 1870.6257 | 2672.3224 | 3474.0191 | 2431.8134 | 3474.0191 | 4516.2248 | 2939.5546 | 4199.3637 | 5459.1729 | 3634.3584 | 5191.9406 | 6749.5228 | 2993.0011 | 4275.7158 | 5558.4305 | Based on lower bound cost in CAR (2017) | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. Glew, D., Parker, D., Miles-Shenton, D., Fletcher, M., Thomas, F., Booth, J., Cobden, L., (Fourthcoming). Thin Internal Wall Insulation (TIWI) Project. | Converted from 2016 prices
4 | Easy to treat cavities (Unfilled)* | 241.2513 | 344.6448 | 448.0382 | 241.2513 | 344.6448 | 448.0382 | 241.2513 | 344.6448 | 448.0382 | 296.9247 | 424.1782 | 551.4316 | 386.0021 | 551.4316 | 716.8611 | 400.8484 | 572.6405 | 744.4327 | 482.5027 | 689.2895 | 896.0764 | 371.1559 | 530.2227 | 689.2895 | Based on lower bound cost in CAR (2017) | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. | Converted from 2016 prices
6 | Partially filled cavities | 2041.3574 | 2916.2248 | 3791.0923 | 2041.3574 | 2916.2248 | 3791.0923 | 2041.3574 | 2916.2248 | 3791.0923 | 2598.0912 | 3711.5589 | 4825.0265 | 3377.5186 | 4825.0265 | 6272.5345 | 4082.7147 | 5832.4496 | 7582.1845 | 5047.72 | 7211.0286 | 9374.3372 | 4156.9459 | 5938.4942 | 7720.0424 | Based on lower bound cost in CAR (2017) | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. | Converted from 2016 prices
7 | Loft insulation* | 154.0297 | 220.0424 | 286.0551 | 154.0297 | 220.0424 | 286.0551 | 154.0297 | 220.0424 | 286.0551 | 141.0392 | 201.4846 | 261.93 | 183.351 | 261.93 | 340.509 | 144.7508 | 206.7869 | 268.8229 | 193.0011 | 275.7158 | 358.4305 | 319.1941 | 455.9915 | 592.789 | Based on lower bound cost in CAR (2017) | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. | Converted from 2016 prices
9 | Suspended timber floor insulation | 2173.5 | 3105 | 4036.5 | 1732.5 | 2475 | 3217.5 | 1732.5 | 2475 | 3217.5 | 1275.75 | 1822.5 | 2369.25 | 1354.5 | 1935 | 2515.5 | 1464.75 | 2092.5 | 2720.25 | 2378.25 | 3397.5 | 4416.75 | 2425.5 | 3465 | 4504.5 | Based on lower bound cost in CAR (2017) :£1/m2 plus 500 fixed cost | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. | 2019 Price year
10 | Solid floor insulation | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 1417.5 | 2025 | 2632.5 | 1505 | 2150 | 2795 | 1627.5 | 2325 | 3022.5 | 2642.5 | 3775 | 4907.5 | 2695 | 3850 | 5005 | Based on Cardiff University (2019): £50/m2 | Cardiff University, 2019. Homes of today for tomorrow - Decarbonising Welsh Housing between 2020 and 2050. | 2019 Price year
11 | Secondary glazing* | 1558.8547 | 2226.9353 | 2895.0159 | 1558.8547 | 2226.9353 | 2895.0159 | 1558.8547 | 2226.9353 | 2895.0159 | 2969.2471 | 4241.7815 | 5514.316 | 3860.0212 | 5514.316 | 7168.6108 | 4008.4836 | 5726.4051 | 7444.3266 | 4453.8706 | 6362.6723 | 8271.474 | 4305.4083 | 6150.5832 | 7995.7582 | Aligned with double glazing costs | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. | Converted from 2016 prices
12 | Double glazing * | 1558.8547 | 2226.9353 | 2895.0159 | 1558.8547 | 2226.9353 | 2895.0159 | 1558.8547 | 2226.9353 | 2895.0159 | 2969.2471 | 4241.7815 | 5514.316 | 3860.0212 | 5514.316 | 7168.6108 | 4008.4836 | 5726.4051 | 7444.3266 | 4453.8706 | 6362.6723 | 8271.474 | 4305.4083 | 6150.5832 | 7995.7582 | Based on lower bound cost in CAR (2017) | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. | Converted from 2016 prices
13 | Double Glazing- Slim profile* | 1870.6257 | 2672.3224 | 3474.0191 | 1870.6257 | 2672.3224 | 3474.0191 | 1870.6257 | 2672.3224 | 3474.0191 | 3563.0965 | 5090.1379 | 6617.1792 | 4632.0255 | 6617.1792 | 8602.333 | 4810.1803 | 6871.6861 | 8933.1919 | 5344.6448 | 7635.2068 | 9925.7688 | 5166.4899 | 7380.6999 | 9594.9099 | 20% uplift on double glazing costs | Heath, N., Baker, P., Menzies, G., 2010. Slim‐profile double glazing: Thermal performance and embodied energy. Historic Scotland. | Converted from 2016 prices
14 | Triple Glazing* | 1909.597 | 2727.9958 | 3546.3945 | 1909.597 | 2727.9958 | 3546.3945 | 1909.597 | 2727.9958 | 3546.3945 | 3637.3277 | 5196.1824 | 6755.0371 | 4728.526 | 6755.0371 | 8781.5483 | 4910.3924 | 7014.8462 | 9119.3001 | 5455.9915 | 7794.2736 | 10132.5557 | 5274.1251 | 7534.4645 | 9794.8038 | 22.5% uplift on double glazing costs | CAR, 2017. What Does It Cost to Retrofit Homes? Department for Business, Energy & Industrial Strategy. | Converted from 2016 prices
15 | Insulated doors | 0 | 0 | 0 | 411.2554 | 411.2554 | 411.2554 | 0 | 0 | 0 | 411.2554 | 822.5108 | 822.5108 | 411.2554 | 822.5108 | 822.5108 | 411.2554 | 822.5108 | 822.5108 | 411.2554 | 822.5108 | 822.5108 | 411.2554 | 822.5108 | 822.5108 | Based on lower bound in Rickaby (2017) | Rickaby (2017) CAPITAL COSTS OF ENERGY IMPROVEMENT MEASURES.Savills | Converted from 2015 prices
Uncertainty |  |  |  |  | Low |  | Medium |  | High
Deep Retrofit Package Costs
Cost | Wall | Glazing | Other | Roof (CCC low-bound avg. value) | Floor | Survey and design | Site Costs | Prelims | OH&P | Assumption & Sourcing
Cost values aligned to internal modelling measure names | 6342.9829 | 6702.6148 | 4979.7723 | 719.4088 | 4352.3338 | These non-measure costs have been subsumed proportionally into the measure costs presented to the left. |  |  |  | Costs based on evidence provided by Energiesprong, representing a view of the cost reductions that might be achievable in deep retrofits, with adjustments made to align with CCC modelling approach. It should be noted that the costs do not reflect an Energiesprong retrofit. This modelling of deep retrofits differs from the Energiesprong model in a number of important ways; amongst other things we do not model onsite generation or lifetime net maintenance costs which are core to the Energiesprong business case. For further discussion of the benefits of the Energiesprong retrofit model see CCC (2018) UK housing: Fit for the future? Costs provided are applicable to a medium, terraced dwelling and are scaled in modelling as relevant when applied to other dwelling types. Deep retrofits are not modelled for high-rise flats and listed buildings.
Lifetimes
| Measures/ size | Lifetime (years) | Source | Notes
1 | Solid wall insulation (External)* | 36 | OFGEM - ECO3: https://www.ofgem.gov.uk/system/files/docs/2018/12/eco3_measures_table_v3.1.pdf | Measure lifetimes not noted here are considered as 30 years based on previous modelling work conducted in the 5CB.
2 | Solid wall insulation (Internal)* | 36
3 | Solid Wall insulation (Thin)* | 36
4 | Easy to treat cavities (Unfilled)* | 42
5 | Hard to treat cavities (Unfilled)* | 42
6 | Partially filled cavities | 42
7 | Loft insulation* | 42
8 | Loft insulation (HTT)* | 42
9 | Suspended timber floor insulation | 42
10 | Solid floor insulation | 42
11 | Secondary glazing* | 20
12 | Double glazing * | 20
13 | Double Glazing- Slim profile* | 20
14 | Triple Glazing* | 20
16 | Draught proofing (draught stripping) | 10

## Energy savings
Fabric Measure Savings
Base savings % (reduction in kWh baseline consumption) - drawn from UCL (2020) Analysis work to refine fabric energy efficiency assumptions for use in developing the Sixth Carbon Budget, using NEED kWh savings, set against NEED total gas baseline consumption.
|  | Flat CNV |  |  | Flat LR |  |  | Flat HR |  |  | Mid Terrace |  |  | End Terrace |  |  | Semi Detached |  |  | Detached |  |  | Bungalow |  |  | Sources | Main source of data anlaysis | Adjustment incorprating case study data
| Measures/ size | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L | Main Sources of data
1 | External (solid) wall insulation | 14.49% | 14.49% | 14.49% | 20.13% | 20.13% | 20.13% | 20.13% | 20.13% | 20.13% | 10.17% | 10.17% | 10.17% | 13.44% | 13.44% | 13.44% | 14.95% | 14.95% | 14.95% | 14.48% | 14.48% | 14.48% | 10.99% | 10.99% | 10.99% | BEIS (2019) National Energy Efficiency Data Framework (NEED): Impact of Measures- Solid Wall Installations 2016. | University College London (UCL), 2020. Analysis Work to Refine Fabric Energy Efficiency Assumptions for use in Developing the Sixth Carbon Budget. | Non- NEED data low uncertainty & limited CS data
2 | Internal (solid) wall insulation | 12.25% | 12.25% | 12.25% | 17.01% | 17.01% | 17.01% | 17.01% | 17.01% | 17.01% | 8.593% | 8.593% | 8.593% | 11.36% | 11.36% | 11.36% | 12.63% | 12.63% | 12.63% | 12.23% | 12.23% | 12.23% | 9.286% | 9.286% | 9.286% | BEIS (2019) National Energy Efficiency Data Framework (NEED): Impact of Measures- Solid Wall Inallations 2017 |  | Non- NEED data low uncertainty & limited CS data
3 | Thin internal (solid) wall insulation | 11.76% | 11.76% | 11.76% | 16.33% | 16.33% | 16.33% | 16.33% | 16.33% | 16.33% | 8.249% | 8.249% | 8.249% | 10.9% | 10.9% | 10.9% | 12.12% | 12.12% | 12.12% | 11.74% | 11.74% | 11.74% | 8.914% | 8.914% | 8.914% | BEIS (2019) National Energy Efficiency Data Framework (NEED): Impact of Measures- Solid Wall Installations 2016. Glew, D., Parker, D., Miles-Shenton, D., Fletcher, M., Thomas, F., Booth, J., Cobden, L. for BEIS, (Forthcoming). Thin Internal Wall Insulation (TIWI) Project. |  | N/A
4 | Easy to treat cavities (Unfilled) | 10.63% | 10.63% | 10.63% | 14.77% | 14.77% | 14.77% | 14.77% | 14.77% | 14.77% | 4.237% | 4.237% | 4.237% | 7.115% | 7.115% | 7.115% | 8.541% | 8.541% | 8.541% | 11.26% | 11.26% | 11.26% | 8.059% | 8.059% | 8.059% | BEIS (2019) National Energy Efficiency Data Framework (NEED): Impact of Measures- Cavity Wall Installations 2016. |  | Non- generally within range
5 | Hard to treat cavities (Unfilled) | 10.63% | 10.63% | 10.63% | 14.77% | 14.77% | 14.77% | 14.77% | 14.77% | 14.77% | 4.237% | 4.237% | 4.237% | 7.115% | 7.115% | 7.115% | 8.541% | 8.541% | 8.541% | 11.26% | 11.26% | 11.26% | 8.059% | 8.059% | 8.059% | BEIS (2019) National Energy Efficiency Data Framework (NEED): Impact of Measures- Cavity Wall Installations 2016. |  | Non- CS data against control group
6 | Partially filled cavities | 12.25% | 12.25% | 12.25% | 17.01% | 17.01% | 17.01% | 17.01% | 17.01% | 17.01% | 8.593% | 8.593% | 8.593% | 11.36% | 11.36% | 11.36% | 12.63% | 12.63% | 12.63% | 12.23% | 12.23% | 12.23% | 9.286% | 9.286% | 9.286% | BEIS (2019) National Energy Efficiency Data Framework (NEED): Impact of Measures- Solid Wall Inallations 2017 |  | Non- NEED data low uncertainty & no CS data
7 | Loft insulation (see loft potential factor in below section) | 7.729% | 7.729% | 7.729% | 10.74% | 10.74% | 10.74% | 0% | 0% | 0% | 5.085% | 5.085% | 5.085% | 3.162% | 3.162% | 3.162% | 3.559% | 3.559% | 3.559% | 4.826% | 4.826% | 4.826% | 5.861% | 5.861% | 5.861% | BEIS (2019) National Energy Efficiency Data Framework (NEED): Impact of Measures- Loftl Installations 2016. |  | Non- generally within range
8 | Loft insulation (HTT) (see loft potential factor in below section) | 7.729% | 7.729% | 7.729% | 10.74% | 10.74% | 10.74% | 0% | 0% | 0% | 5.085% | 5.085% | 5.085% | 3.162% | 3.162% | 3.162% | 3.559% | 3.559% | 3.559% | 4.826% | 4.826% | 4.826% | 5.861% | 5.861% | 5.861% | BEIS (2019) National Energy Efficiency Data Framework (NEED): Impact of Measures- Loftl Installations 2016. |  | N/A
9 | Suspended timber floor insulation | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | BEIS (2015) National Energy Efficiency Data Framework (NEED): Energy Performance Certificate Analysis & Pelsmakers, S., Elwell, C.A., 2017. Suspended timber ground floors: Heat loss reduction potential of insulation interventions. Energy and Buildings 153, 549–563. https://doi.org/10.1016/j.enbuild.2017.07.085 |  | Non- generally within range for archetype-For 2 storey dwellings only ground floor is insulated
10 | Solid floor insulation | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | 8% | BEIS (2015) National Energy Efficiency Data Framework (NEED): Energy Performance Certificate Analysis & Pelsmakers, S., Elwell, C.A., 2017. Suspended timber ground floors: Heat loss reduction potential of insulation interventions. Energy and Buildings 153, 549–563. https://doi.org/10.1016/j.enbuild.2017.07.085 |  | N/A-For 2 storey dwellings only ground floor is insulated
11.a | Secondary glazing (From Band G) | 6.928% | 4.849% | 3.73% | 7.554% | 5.288% | 4.068% | 7.554% | 5.288% | 4.068% | 6.828% | 4.78% | 3.677% | 6.179% | 4.325% | 3.327% | 5.982% | 4.187% | 3.221% | 9.808% | 6.866% | 5.281% | 6.946% | 4.863% | 3.74% | BFRC (2019) British Fenestration Rating Council. |  | Follows pattern of over estimation of glazing savings - 35% reduction applied across glazing types
11.b | Secondary glazing (From Band E) | 3.149% | 2.204% | 1.696% | 3.434% | 2.404% | 1.849% | 3.434% | 2.404% | 1.849% | 3.104% | 2.173% | 1.671% | 2.809% | 1.966% | 1.512% | 2.719% | 1.903% | 1.464% | 4.458% | 3.121% | 2.401% | 3.157% | 2.21% | 1.7% | BFRC (2019) British Fenestration Rating Council. |  | Follows pattern of over estimation of glazing savings - 35% reduction applied across glazing types
12.a | Double glazing (From Band G) | 7.461% | 5.222% | 4.017% | 8.135% | 5.695% | 4.381% | 8.135% | 5.695% | 4.381% | 7.353% | 5.147% | 3.96% | 6.655% | 4.658% | 3.583% | 6.442% | 4.509% | 3.469% | 10.56% | 7.394% | 5.688% | 7.481% | 5.237% | 4.028% | BFRC (2019) British Fenestration Rating Council. |  | Follows pattern of over estimation of glazing savings - 30% reduction applied across glazing types
12.b | Double glazing (From Band E) | 3.391% | 2.374% | 1.826% | 3.698% | 2.589% | 1.991% | 3.698% | 2.589% | 1.991% | 3.342% | 2.34% | 1.8% | 3.025% | 2.117% | 1.629% | 2.928% | 2.05% | 1.577% | 4.801% | 3.361% | 2.585% | 3.4% | 2.38% | 1.831% | BFRC (2019) British Fenestration Rating Council. |  | Follows pattern of over estimation of glazing savings - 30% reduction applied across glazing types
13.a | Double Glazing- Slim profile (From Band G) | 6.782% | 4.748% | 3.652% | 7.396% | 5.177% | 3.982% | 7.396% | 5.177% | 3.982% | 6.685% | 4.679% | 3.6% | 6.05% | 4.235% | 3.257% | 5.856% | 4.099% | 3.153% | 9.602% | 6.722% | 5.171% | 6.801% | 4.761% | 3.662% | BFRC (2019) British Fenestration Rating Council. |  | Follows pattern of over estimation of glazing savings - 30% reduction applied across glazing types
13.b | Double Glazing- Slim profile (From Band E) | 2.713% | 1.899% | 1.461% | 2.958% | 2.071% | 1.593% | 2.958% | 2.071% | 1.593% | 2.674% | 1.872% | 1.44% | 2.42% | 1.694% | 1.303% | 2.342% | 1.64% | 1.261% | 3.841% | 2.689% | 2.068% | 2.72% | 1.904% | 1.465% | BFRC (2019) British Fenestration Rating Council. |  | Follows pattern of over estimation of glazing savings - 30% reduction applied across glazing types
14.a | Triple Glazing (From Band G) | 9.495% | 6.647% | 5.113% | 10.35% | 7.248% | 5.575% | 10.35% | 7.248% | 5.575% | 9.359% | 6.551% | 5.039% | 8.469% | 5.929% | 4.56% | 8.199% | 5.739% | 4.415% | 13.44% | 9.41% | 7.239% | 9.521% | 6.665% | 5.127% | BFRC (2019) British Fenestration Rating Council. |  | Follows pattern of over estimation of glazing savings - 30% reduction applied across glazing types
14.b | Triple Glazing (From Band E) | 5.426% | 3.798% | 2.922% | 5.917% | 4.142% | 3.186% | 5.917% | 4.142% | 3.186% | 5.348% | 3.744% | 2.88% | 4.84% | 3.388% | 2.606% | 4.685% | 3.279% | 2.523% | 7.682% | 5.377% | 4.136% | 5.441% | 3.808% | 2.93% | BFRC (2019) British Fenestration Rating Council. |  | Follows pattern of over estimation of glazing savings - 30% reduction applied across glazing types
15 | Insulated doors | 0% | 0% | 0% | 2.685% | 1.879% | 1.446% | 0% | 0% | 0% | 1.695% | 2.373% | 1.825% | 1.581% | 2.213% | 1.703% | 1.423% | 1.993% | 1.533% | 1.072% | 1.501% | 1.155% | 1.465% | 2.051% | 1.578% | BFRC (2019) British Fenestration Rating Council. |  | N/A
16 | Draught proofing (draught stripping) | 2.359% | 2.738% | 3.009% | 2.359% | 2.738% | 3.009% | 2.359% | 2.738% | 3.009% | 2.88% | 2.967% | 3.055% | 2.7% | 2.769% | 2.838% | 2.689% | 2.756% | 2.799% | 2.425% | 2.462% | 2.485% | 2.257% | 2.325% | 2.373% | BEIS (2015) National Energy Efficiency Data Framework (NEED): Energy Performance Certificate Analysis . ETI, 2013. Single dweling implementation plan. Energy Technologies Institute. |  | N/A
17 | Reduced infiltration (foam, strips, sealent use) | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | 2% | BEIS (2015) National Energy Efficiency Data Framework (NEED): Energy Performance Certificate Analysis . |  | N/A
18 | HW Tank insulation | 5.575% | 4.455% | 3.356% | 5.575% | 4.455% | 3.356% | 5.575% | 4.455% | 3.356% | 4.156% | 3.836% | 3.516% | 3.522% | 3.238% | 2.953% | 2.989% | 2.65% | 2.349% | 2.345% | 2.06% | 1.803% | 3.006% | 2.66% | 2.353% | BEIS (2015) National Energy Efficiency Data Framework (NEED): Energy Performance Certificate Analysis . Ofgem (2008) Energy Saving Matrix |  | N/A
19 | Ventilation | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | N/A |  | N/A
20 | Shading | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | N/A |  | N/A
Uncertainty |  |  |  |  | Low |  | Medium |  | High
Applied savings % (reduction kWh baseline consumption), after adjusting to rebase against relevant component of gas demand (space heat or hot water depending on measure). Performance gap uplift not included.
|  | Flat CNV |  |  | Flat LR |  |  | Flat HR |  |  | Mid Terrace |  |  | End Terrace |  |  | Semi Detached |  |  | Detached |  |  | Bungalow |  |  | Source & Method
| Measures/ size | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L | S | M | L
1 | External (solid) wall insulation | 18.32% | 18.1% | 17.29% | 25.44% | 25.15% | 24.02% | 25.44% | 25.15% | 24.02% | 12.59% | 12.43% | 11.93% | 16.63% | 16.42% | 15.76% | 18.44% | 18.13% | 17.24% | 17.69% | 17.41% | 16.59% | 13.43% | 13.22% | 12.59% | This table is derived from the table above by adjusting the savings values to rebase them against relevant component of gas demand (space heat or hot water depending on measure). Performance gap uplift is not included in here. A [space heating]:[hot water] ratio was determined (based on the heating demands present in this work's archetype modelling), disaggregated by property type and property size. This ratio was then used to determine the relevant correction factors that were then applied to the savings from the table above, such that the savings in this table reflect a savings against the relevant baseline (e.g. space heating demand, rather than overall gas demand).
2 | Internal (solid) wall insulation | 15.48% | 15.3% | 14.61% | 21.5% | 21.25% | 20.3% | 21.5% | 21.25% | 20.3% | 10.64% | 10.5% | 10.08% | 14.06% | 13.88% | 13.32% | 15.58% | 15.32% | 14.57% | 14.95% | 14.71% | 14.02% | 11.35% | 11.17% | 10.64%
3 | Thin internal (solid) wall insulation | 14.86% | 14.69% | 14.02% | 20.64% | 20.4% | 19.48% | 20.64% | 20.4% | 19.48% | 10.21% | 10.08% | 9.676% | 13.49% | 13.32% | 12.79% | 14.96% | 14.71% | 13.99% | 14.35% | 14.12% | 13.46% | 10.89% | 10.72% | 10.21%
4 | Easy to treat cavities (Unfilled) | 13.43% | 13.28% | 12.68% | 18.66% | 18.44% | 17.61% | 18.66% | 18.44% | 17.61% | 5.245% | 5.177% | 4.97% | 8.807% | 8.693% | 8.345% | 10.53% | 10.36% | 9.852% | 13.76% | 13.54% | 12.9% | 9.847% | 9.691% | 9.234%
5 | Hard to treat cavities (Unfilled) | 13.43% | 13.28% | 12.68% | 18.66% | 18.44% | 17.61% | 18.66% | 18.44% | 17.61% | 5.245% | 5.177% | 4.97% | 8.807% | 8.693% | 8.345% | 10.53% | 10.36% | 9.852% | 13.76% | 13.54% | 12.9% | 9.847% | 9.691% | 9.234%
6 | Partially filled cavities | 15.48% | 15.3% | 14.61% | 21.5% | 21.25% | 20.3% | 21.5% | 21.25% | 20.3% | 10.64% | 10.5% | 10.08% | 14.06% | 13.88% | 13.32% | 15.58% | 15.32% | 14.57% | 14.95% | 14.71% | 14.02% | 11.35% | 11.17% | 10.64%
7 | Loft insulation (see loft potential factor in below section) | 9.768% | 9.655% | 9.221% | 13.57% | 13.41% | 12.81% | 0% | 0% | 0% | 6.294% | 6.213% | 5.964% | 3.914% | 3.864% | 3.709% | 4.39% | 4.316% | 4.105% | 5.897% | 5.803% | 5.53% | 7.161% | 7.048% | 6.716%
8 | Loft insulation (HTT) (see loft potential factor in below section) | 9.768% | 9.655% | 9.221% | 13.57% | 13.41% | 12.81% | 0% | 0% | 0% | 6.294% | 6.213% | 5.964% | 3.914% | 3.864% | 3.709% | 4.39% | 4.316% | 4.105% | 5.897% | 5.803% | 5.53% | 7.161% | 7.048% | 6.716%
9 | Suspended timber floor insulation | 10.11% | 9.993% | 9.543% | 10.11% | 9.993% | 9.543% | 10.11% | 9.993% | 9.543% | 9.903% | 9.775% | 9.384% | 9.903% | 9.775% | 9.384% | 9.868% | 9.703% | 9.228% | 9.775% | 9.621% | 9.167% | 9.775% | 9.621% | 9.167%
10 | Solid floor insulation | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | N/A | 9.903% | 9.775% | 9.384% | 9.903% | 9.775% | 9.384% | 9.868% | 9.703% | 9.228% | 9.775% | 9.621% | 9.167% | 9.775% | 9.621% | 9.167%
11.a | Secondary glazing (From Band G) | 8.755% | 6.058% | 4.45% | 9.547% | 6.606% | 4.852% | 9.547% | 6.606% | 4.852% | 8.452% | 5.84% | 4.313% | 7.649% | 5.285% | 3.903% | 7.378% | 5.078% | 3.715% | 11.98% | 8.257% | 6.052% | 8.488% | 5.848% | 4.286%
11.b | Secondary glazing (From Band E) | 3.98% | 2.753% | 2.023% | 4.339% | 3.003% | 2.206% | 4.339% | 3.003% | 2.206% | 3.842% | 2.655% | 1.96% | 3.477% | 2.402% | 1.774% | 3.354% | 2.308% | 1.689% | 5.448% | 3.753% | 2.751% | 3.858% | 2.658% | 1.948%
12.a | Double glazing (From Band G) | 9.428% | 6.524% | 4.792% | 10.28% | 7.114% | 5.226% | 10.28% | 7.114% | 5.226% | 9.102% | 6.289% | 4.644% | 8.237% | 5.692% | 4.203% | 7.946% | 5.469% | 4.001% | 12.91% | 8.892% | 6.518% | 9.141% | 6.297% | 4.616%
12.b | Double glazing (From Band E) | 4.286% | 2.965% | 2.178% | 4.673% | 3.233% | 2.375% | 4.673% | 3.233% | 2.375% | 4.137% | 2.859% | 2.111% | 3.744% | 2.587% | 1.91% | 3.612% | 2.486% | 1.819% | 5.867% | 4.042% | 2.963% | 4.155% | 2.862% | 2.098%
13.a | Double Glazing- Slim profile (From Band G) | 8.571% | 5.931% | 4.357% | 9.346% | 6.467% | 4.751% | 9.346% | 6.467% | 4.751% | 8.275% | 5.718% | 4.222% | 7.488% | 5.174% | 3.821% | 7.223% | 4.972% | 3.637% | 11.73% | 8.084% | 5.925% | 8.31% | 5.725% | 4.196%
13.b | Double Glazing- Slim profile (From Band E) | 3.429% | 2.372% | 1.743% | 3.739% | 2.587% | 1.9% | 3.739% | 2.587% | 1.9% | 3.31% | 2.287% | 1.689% | 2.995% | 2.07% | 1.528% | 2.889% | 1.989% | 1.455% | 4.693% | 3.233% | 2.37% | 3.324% | 2.29% | 1.678%
14.a | Triple Glazing (From Band G) | 12% | 8.303% | 6.099% | 13.08% | 9.054% | 6.651% | 13.08% | 9.054% | 6.651% | 11.58% | 8.005% | 5.911% | 10.48% | 7.244% | 5.349% | 10.11% | 6.961% | 5.092% | 16.43% | 11.32% | 8.295% | 11.63% | 8.015% | 5.875%
14.b | Triple Glazing (From Band E) | 6.857% | 4.744% | 3.485% | 7.477% | 5.174% | 3.8% | 7.477% | 5.174% | 3.8% | 6.62% | 4.574% | 3.378% | 5.991% | 4.139% | 3.057% | 5.779% | 3.978% | 2.91% | 9.387% | 6.467% | 4.74% | 6.648% | 4.58% | 3.357%
15 | Insulated doors | 0% | 0% | 0% | 3.393% | 2.347% | 1.724% | 0% | 0% | 0% | 2.098% | 2.899% | 2.141% | 1.957% | 2.705% | 1.997% | 1.756% | 2.417% | 1.768% | 1.31% | 1.806% | 1.323% | 1.79% | 2.467% | 1.808%
16 | Draught proofing (draught stripping) | 2.981% | 3.42% | 3.589% | 2.981% | 3.42% | 3.589% | 2.981% | 3.42% | 3.589% | 3.565% | 3.626% | 3.583% | 3.342% | 3.383% | 3.329% | 3.317% | 3.342% | 3.229% | 2.963% | 2.96% | 2.848% | 2.758% | 2.796% | 2.719%
17 | Reduced infiltration (foam, strips, sealent use) | 2.527% | 2.498% | 2.386% | 2.527% | 2.498% | 2.386% | 2.527% | 2.498% | 2.386% | 2.476% | 2.444% | 2.346% | 2.476% | 2.444% | 2.346% | 2.467% | 2.426% | 2.307% | 2.444% | 2.405% | 2.292% | 2.444% | 2.405% | 2.292%
18 | HW Tank insulation | 7.046% | 5.565% | 4.003% | 7.046% | 5.565% | 4.003% | 7.046% | 5.565% | 4.003% | 5.144% | 4.687% | 4.124% | 4.36% | 3.956% | 3.464% | 3.687% | 3.214% | 2.709% | 2.866% | 2.478% | 2.066% | 3.673% | 3.199% | 2.696%
19 | Ventilation | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
20 | Shading | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
Uncertainty |  |  |  |  | Low |  | Medium |  | High
Loft Potential Factor
Disaggregated Loft Attribute Type (based on level of existing insulation) | Loft Potential Factor | Source & Method | [5 empty] | Assumptions
No roof | 0 | Based on calibration to the actual observed savings data for loft insulation measures from NEED and using the difference in U-values (of insulated and non-insulated levels) using SAP Table S9. i.e. the caclulation method uses the NEED data distribution of thicknesses up to and including 100mm (as a starting point) and determines the savings for insulation to around 270mm-300mm based on changes in U-value. | [5 empty] | All savings for lofts (in the above table) are applied in conjunction with a loft potential factor based on the disaggregated loft type (i.e. level of existing insulation). For example, the savings for a loft inulsation measure in a medium, mid-terraced dwelling, which has less than 100mm of existing insulation is [6% * 1.77] = [11%]. Lofts that are categorised as "no roof" or "200mm or more" are considered unsuitable.
Less than 100mm ETT | 1.7684
Less than 100mm HTT | 1.7684
100 -199mm ETT | 0.43295
100 -199mm HTT | 0.43295
200mm or more | 0.08396
Behavioural Measure Savings
Behavioural Measure Savings
Behavioural measure | SH or HW | % Savings | Cost | Assumptions | [11 empty] | Source
Reduction in space heat demand from smarter heating management and use | SH | 3% | Assume all costs are low or negligable (not to be accounted for in modelling) Exception: Widespread Engagement has a £440 cost applied for multi-zone control. | EDRP study suggests 3% savings for gas consumption (which we take here to be heating): https://www.ofgem.gov.uk/ofgem-publications/59105/energy-demand-research-project-final-analysis.pdf
Multizone control | SH | 6.3% |  | - Savings based on studies: ESC, Beizaee et al. measurements, and ESP-r estimates - Stated % savings is the average of all dwelling and tenant/owner types - In some instances, increased usage is seen where residents opt to increase the temperature in one room more significantly for comfort purposes | [11 empty] | Multi-zone control savings sources: https://es.catapult.org.uk/wp-content/uploads/2019/11/SSH1-Pathways-to-Low-Carbon-Heating-Report-FINAL.pdf https://strathprints.strath.ac.uk/58937/1/Cockroft_etal_EB2016_Potential_energy_savings_achievable_by_zoned_control.pdf System cost sources: https://www.hivehome.com/products/hive-active-heating/buy https://www.hivehome.com/products/hive-radiator-valve https://www.loxone.com/enen/multi-zone-heating-a-better-alternative-to-smart-thermostats/
Regulated/Low flow shower head | HW | 5.3% |  | - Accounts for portion of GB homes that are able to adopt (40%) - Accounts for a portion of total HW demand being attributed to showers (20%) - Uses difference in standard shower head (18L/min) vs. low-flow shower head (6L/min) flow rates | [11 empty] | Portion of GB stock able to adopt measure: https://cambridgeenergy.org.uk/wp-content/uploads/2013/11/CAR-Behaviours-Final-Report-Revision-3-060812.pdf Portion of overall energy used for HW attributed to showers: https://waterwise.org.uk/save-water/ Shower flow rates: https://www.hotwater.org.uk/sizing-a-hot-water-cylinder/ https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/482120/gbs-taps-automatic-sprays-showers-urinal-2015.pdf https://www.scottishwater.co.uk/en/Your-Home/Save-Water/Water-Saving-Devices
Heat as a service (HaaS) | SH | See assumptions |  | 7.5% cost of capital (against a default value of 3.5%) based on the HaaS model being operated commercially, and thus using a commercial discount rate, as opposed to a domestic rate. 3% financial savings (best-case figure) based on external modelling assumptions such as: future generation mix, wholesale market costs, future charging mechanisms for network costs and other schemes, and building archetype. 5% increase in total heating demandis expected for this demand side management approach, which involves significant time-shifting of heat demand, due to households losing heat to the environment for longer periods of time. However, it should be noted that increases in demand are more likely when energy is more abundant and/or less carbon intensive; studies show reduced peaks for electricity demand, which could also result in the potential to reduce investment needed in network reinforcement. 15% increase in heat pump efficiency based on the wide range of potential efficiencies available for heat pumps and the assumption that large-scale providers (in contrast with individual residents) will have better installation and operational processes that enable this increase in efficiency. | [11 empty] | 7.5% cost of capital: Standard Green book commerical declining discount rate. 3% financial savings: Energy Systems Catapult: EPO simulating Heat as a Service for Demand-Side Management (2019) . 5% increase in energy consumption: Energy Systems Catapult (2019) Smart Systems and Heat Phase 2 D10 - D14: Market Transformations Report. These findings are sensitive to assumptions regarding future market structures and service propositions. 15% increase in heat pump operating efficiency: based on expert feedback via external stakeholder discussion.
Deep Retrofit Package Savings
Package Savings |  |  | Assumptions & Sourcing
The savings of a deep retrofit package are modelled using a different methodology than how standard fabric or behavioural measures are modelled. The deep retrofits applied in the modelling achieve a 40 kWh/m2/yr space heating demand goal, rather than a specified savings percentage. This could be anywhere from 0% (where a dwelling is already achieving this goal, and so is not suited to further retrofitting) to 80% (for a disproportionaly under insulated dwelling which has the highest potential for savings). Dependent on the type of dwellings which take up these deep retrofit packages, it may be that, on average, up to 57% of energy efficiency savings can be achieved. |  |  | Assumptions for deep whole house retrofits informed by evidence provided by Energiesprong. It should be noted that our modelling of deep retrofits differs from the Energiesprong model in a number of important ways; notably we do not model onsite generation or counterfactual maintenance costs which are core to the Energiesprong business case. For further discussion of the benefits of the Energiesprong retrofit model see CCC (2018) UK housing: Fit for the future? Savings provided are exemplary and dependent on a dwellings inital heating demand, insulation levels, and potential for retrofit. Deep retrofits not modelled for high-rise flats and listed buildings.

## Technology base costs
All costs are expressed in a base year of £2019 (converted from the source data where appropriate).
[5 empty] | Fixed (£) |  |  |  |  | Marginal (£/kW) |  |  |  |  | OPEX (£/y)
Simple name | Technology | Minimum size (kW) | Sizing increments (kW) | Lifetime (y) | 2015 | 2020 | 2030 | 2040 | 2050 | 2015 | 2020 | 2030 | 2040 | 2050 | All years | Assumptions | [7 empty] | Source
Electric resistive | Electric resistive heating | 1.5 | 1.5 | 15 | 235.7773 | 235.7773 | 235.7773 | 235.7773 | 235.7773 | 117.3693 | 117.3693 | 117.3693 | 117.3693 | 117.3693 | 103.8666 | Converts originally assumed NZ costs to 2019 values. | [7 empty] | BEIS: Evidence gathering for electric heating options in off gas grid homes (2019) https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/831079/Electric_heating_options_in_off-gas_grid_homes.pdf Assumptions unchanged from Net Zero, with lifetime and opex assumptions aligned to Fifth Carbon Budget (flat rate opex assumed across non-hybrid technologies).
Storage heater | Storage heater | 1 | 1 | 15 | [5 empty] | 778.9997 | 778.9997 | 778.9997 | 778.9997 | 778.9997 | 103.8666 | 1 kW demand is equivalent to 15 kWh installed storage heaters Converts originally assumed NZ costs to 2019 values.
Low carbon heat networks | District heating - heat interface unit and heat meter | 3 | 1 | 15 | Costs implicit in the fuel cost assumptions. | [9 empty] | 103.8666 | No differences in technology cost. Fuel cost/types vary by scenario: Electricity peaking fuel used in all scenarios except Headwinds (no contribution from Hydrogen or Gas). Headwinds uses natural gas peaking fuel before grid conversion to hydrogen and hydrogen peaking fuel after grid conversion. Details covered in the Fuel costs and CO2 tab. Heat interface unit and heat meter costs implicit in the fuel costs. Converts originally assumed NZ costs to 2019 values. | [7 empty] | Calculated from modelling results based on District heating and local apporaches to heat decarbonisation (2015) Element Energy for CCC. Opex assumptions aligned to Fifth Carbon Budget (flat rate opex assumed across non-hybrid technologies).
Gas boiler | Gas boiler | See below |  | 15 | See below. | [9 empty] | 103.8666 | See below. | [7 empty] | Lifetime assumptions aligned to Fifth Carbon Budget. Opex assumptions aligned to Fifth Carbon Budget (flat rate opex assumed across non-hybrid technologies).See below for wider sources.
Oil boiler | Oil boiler |  |  | 15 | [10 empty] | 103.8666
Hydrogen boiler | Hydrogen boiler (Hydrogen-only boiler and Hyready boiler) |  |  | 15 | [10 empty] | 103.8666 | Based on findings that pre-mixed combustion of hydrogen (i.e. in domestic boilers) is typically lower NOX than natural gas. | [7 empty] | Hydrogen supply chain evidence base, Report for BEIS (2018) Opex assumptions aligned to Fifth Carbon Budget (flat rate opex assumed across non-hybrid technologies), no further uplift based on findings that pre-mixed combustion of hydrogen (i.e. in domestic boilers) is typically lower NOX than natural gas (Gersen, S. Darmeveil, H. Van Essen, M. Martinus, G.H. and Teerlingc, O.J (2020) Domestic hydrogen boilers in practice: enabling the use of hydrogen in the built environment. These findings are supported by testing currently being undertaken by Worcester Bosch).
Fixed (£)
| Year | 2020
Simple name | Boiler type / size (kW) | 12 | 15 | 18 | 24 | 28 | 32 | 36 | 40 | 44 | 48 | 52 | 56 | 60 | OPEX (£/y) | Assumptions | [7 empty] | Source
Gas boiler | Gas boiler (regional installer, including labour, controls, and fittings and heat distribution system) | 2664.02 | 2719.01 | 2774 | 2864 | 3341.3333 | 3818.6667 | 4296 | 4773.3333 | 5250.6667 | 5728 | 6205.3333 | 6682.6667 | 7160 | 103.8666 | Marginal price for boilers above 24 kW remains the same as that calculated from the 24 kW system price, from the source. Note that in the scenarios, the gas boilers may use the hyready boiler costs below. | [7 empty] | 12 - 15 kW: Based on marginal cost difference between available data in based on the below source. 18 kW & 24 kW: The Cost of Installing Heating Measures in Domestic Properties, Delta-EE for BEIS (2018) (based on 50%:50% weighted average cost of 1) 24kW combi for combi direct swap by regional installer and 2) 24kW non-combi for non-combi direct swap by regional installer). 50%:50% is based on BEIS NHM data which suggests counterfactual stock is 50% combi gas boilers and 50% non-combi gas boilers. >24 kW: Based on ratio of cost (£) to power (kW) of the 24kW system (scaled).
Hydrogen boiler | Hydrogen boiler (Hydrogen-only boiler and Hyready boiler) | 2764.02 | 2819.01 | 2874 | 2964 | 3441.3333 | 3918.6667 | 4396 | 4873.3333 | 5350.6667 | 5828 | 6305.3333 | 6782.6667 | 7260 | 103.8666 | £100 added to cost of gas boiler to account for increased technology and volume cost of Hydrogen boiler | [7 empty] | Hydrogen supply chain evidence base report for BEIS (2018); edited based on feedback from external stakeholders
Oil boiler | Oil boiler (regional installer, including labour, fittings, removal of old equipment but excluding controls and heat distribution system) | 2881.64 | 2943.71 | 3005.78 | 3129.94 | 3651.5967 | 4173.2533 | 4694.91 | 5216.5667 | 5738.2233 | 6259.88 | 6781.5367 | 7303.1933 | 7824.85 | 103.8666 | Marginal price for boilers above 24 kW remains the same as that calculated from the 24 kW system price, from the source. | [7 empty] | 12 - 15 kW: Based on marginal cost difference between available data in based on the below source. 18 kW & 24 kW: The Cost of Installing Heating Measures in Domestic Properties, Delta-EE for BEIS (2018) (based on 14.6%:85.4% weighted average cost of 1) 24kW combi for combi direct swap by regional installer and 2) 24kW non-combi for non-combi direct swap by regional installer). 14.6%:85.4% is based on BEIS NHM data which sugguests counterfactual stock is 14.6% combi gas boilers and 85.4% non-combi gas boilers. >24 kW: Based on ratio of cost (£) to power (kW) of the 24kW system (scaled). Oil boiler capex has been used to represent that of a bio boiler capex; bioboiler capex and fuel costs are intended to be broadly representative for a range of biofuels and should not be taken to suggest recommendations for a particular biofuel.
Solar thermal
| Size of system (kW) | 2020 12: Lifetime (y); 2020 15: 3; 2020 18: 8
Simple name | Maximum hot water supplied (kWh) | 2020 15: 1929; 2020 18: 5144; 2020 24: Assumptions; 2020 48: Source
Solar Thermal | Cost used to derive kWh/kW values for joint heating system plus solar thermal | 2020 12: 25; 2020 15: 3750; 2020 18: 5250; 2020 24: Heat delivered calculated assuming that solar thermal delivers no more than 60% of hot water demand or 643 kWh/kW, whichever is lower. Two configurations made: 1) accounting for 60% of hot water 2) accounting for 60% hot water + 50% space heating. Assume £750 (cost of HW cylinder) is removed from the cost of the RHI prices (to not double count in configurations with ASHP); 2020 48: https://www.gov.uk/government/collections/renewable-heat-incentive-statistics RHI monthly deployment data: December 2019 (Annual edition) Table S2.1 - Average reported costs of domestic RHI installations, Great Britain, April 2014 to December 2019 [Solar thermal data] HW cylinder costs were suggested by external stakeholders to be between £500-£1000 (excl. VAT); link below corroborates https://heatingforce.co.uk/blog/installation-cost-vented-unvented-hot-water-cylinders/ Additionally, all costs were corroborated by analysis undertaken by Dr. Richard Hall (Energy Transitions). Solar thermal Lifetime: 25 years Typically stated ranges are between 20-30 year with most sources noting that warranties are for 20 years while actualy components are likely to last up to 30 years. https://www.isoenergy.co.uk/latest-news/renewable-energy-news-from-isoenergy/how-long-do-solar-panels-last http://thegreenhome.co.uk/heating-renewables/solar-panels/solar-thermal-system-lifespan/ https://www.renewableenergyhub.co.uk/main/solar-thermal-information/solar-thermal-system-lifespan-maintenance-and-warranties/ https://www.cibsejournal.com/cpd/modules/2012-05/
Solar thermal configurations
[5 empty] | Scenario | Balanced Net Zero Pathway / Widespread Engagement / Headwinds | [5 empty] | Widespread Innovation / Tailwinds Scenarios
[5 empty] | Year | 2020 |  | 2030 |  | 2050 |  | 2030 |  | 2050
Simple name | Configuration | Minimum size (kW) | Sizing increments (kW) | OPEX (£/y) | Lifetime (y) | Fixed (£) | Marginal (£/kW) | Fixed (£) | Marginal (£/kW) | Fixed (£) | Marginal (£/kW) | Fixed (£) | Marginal (£/kW) | Fixed (£) | Marginal (£/kW) | Assumptions |  |  |  | Source
ASHP + solar thermal HW | Solar thermal + ASHP: config 1 (60% HW) | 4 | 1 | 157.7333 | 15 / 17 - ASHP (Balanced Net Zero Pathway, Widespread Engagement, Headwinds / Widespread Innovation, Tailwinds) 25 - solar thermal | 6421.6022 | 445.9096 | 5137.2818 | 371.7846 | 4694.2818 | 334.7221 | 4694.2818 | 334.7221 | 4251.2818 | 297.6596 | Heat delivered calculated assuming that solar thermal delivers no more than 60% of hot water demand or 643 kWh/kW, whichever is lower. Two configurations made: 1) accounting for 60% of hot water 2) accounting for 60% hot water + 50% space heating. Assume £750 (cost of HW cylinder) is removed from the cost of the RHI prices (to not double count in configurations with ASHP) 20% reduction in ASHP capex from 2020 to 2030 in the 6CB Balanced Net Zero Pathway scenario. 30% reduction in ASHP capex from 2020 to 2050 in the 6CB Balanced Net Zero Pathway scenario. 30% reduction in ASHP capex from 2020 to 2030 in the Widespread Innovation/Tailwinds scenarios. 40% reduction in ASHP capex from 2020 to 2050 in the Widespread Innovation/Tailwinds scenarios. 20% reduction in solar thermal capex from 2020 to 2030 in all scenarios. Solar thermal opex modelled the same as a storage heater. Opex assumed to be £50 lower than the sum of the opex for the two components of the hybrid system due to economies of scale. Solar thermal prices that are added here are discounted to account for a same lifetime basis for modelling (i.e. 15 year prices). |  |  |  | Configurations: Input into the modelled configurations: Solar Heat Worldwaide 2018, figure 57 https://www.iea-shc.org/Data/Sites/1/publications/Solar-Heat-Worldwide-2018.pdf This work indicated that SH+HW systems can have lower levelised costs than HW only. Costs: https://www.gov.uk/government/collections/renewable-heat-incentive-statistics RHI monthly deployment data: December 2019 (Annual edition), Table S2.1 - Average reported costs of domestic RHI installations, Great Britain, April 2014 to December 2019, [Solar thermal data] Cost reduction to 2030 suggested by Dr. Richard Hall (Energy Transitions). HW cylinder costs were suggested by Dr. Richard Hall to be between £500-£1000 (excl. VAT); link below corroborates https://heatingforce.co.uk/blog/installation-cost-vented-unvented-hot-water-cylinders/ ASHP Lifetime: EE - Evidence gathering for electric heating options in off gas grid homes - Final Report (2019): https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/831079/Electric_heating_options_in_off-gas_grid_homes.pdf Lifetime and cost reductions in each scenario based on feedback from external heat pump stakeholders.. Solar thermal Lifetime: 25 years Typically stated ranges are between 20-30 year with most sources noting that warranties are for 20 years while actualy components are likely to last up to 30 years. https://www.isoenergy.co.uk/latest-news/renewable-energy-news-from-isoenergy/how-long-do-solar-panels-last http://thegreenhome.co.uk/heating-renewables/solar-panels/solar-thermal-system-lifespan/ https://www.renewableenergyhub.co.uk/main/solar-thermal-information/solar-thermal-system-lifespan-maintenance-and-warranties/ https://www.cibsejournal.com/cpd/modules/2012-05/
ASHP + solar thermal HW/SH | Solar thermal + ASHP: config 2 (60% HW + 50% SH; larger solar array) | 4 | 1 | 157.7333 | 15 / 17 - ASHP (Balanced Net Zero Pathway, Widespread Engagement, Headwinds / Widespread Innovation, Tailwinds) 25 - solar thermal | 6421.6022 | 674.397 | 5137.2818 | 600.272 | 4694.2818 | 563.2095 | 4694.2818 | 563.2095 | 4251.2818 | 526.147
Storage heater + solar thermal HW | Solar thermal + storage heater: config 1 (60% HW) | 1 | 1 | 157.7333 | 15 / 17 - ASHP (Balanced Net Zero Pathway, Widespread Engagement, Headwinds / Widespread Innovation, Tailwinds) 25 - solar thermal | 1991.6022 | 839.1596 | 1593.2818 | 839.1596 | 1593.2818 | 839.1596 | 1593.2818 | 839.1596 | 1593.2818 | 839.1596
Storage heater + solar thermal HW/SH | Solar thermal + storage heater: config 2 (60% HW + 50% SH; larger solar array) | 1 | 1 | 157.7333 | 15 / 17 - ASHP (Balanced Net Zero Pathway, Widespread Engagement, Headwinds / Widespread Innovation, Tailwinds) 25 - solar thermal | 1991.6022 | 1067.647 | 1593.2818 | 1067.647 | 1593.2818 | 1067.647 | 1593.2818 | 1067.647 | 1593.2818 | 1067.647
Electric resistive + solar thermal HW | Solar thermal + electric resistive: config 1 (60% HW) | 1.5 | 1.5 | 157.7333 | 15 / 17 - ASHP (Balanced Net Zero Pathway, Widespread Engagement, Headwinds / Widespread Innovation, Tailwinds) 25 - solar thermal | 2222.8017 | 166.8487 | 1824.4813 | 166.8487 | 1824.4813 | 166.8487 | 1824.4813 | 166.8487 | 1824.4813 | 166.8487
Electric resistive + solar thermal HW/SH | Solar thermal + electric resistive: config 2 (60% HW + 50% SH; larger solar array) | 1.5 | 1.5 | 157.7333 | 15 / 17 - ASHP (Balanced Net Zero Pathway, Widespread Engagement, Headwinds / Widespread Innovation, Tailwinds) 25 - solar thermal | 2222.8017 | 323.9337 | 1824.4813 | 323.9337 | 1824.4813 | 323.9337 | 1824.4813 | 323.9337 | 1824.4813 | 323.9337
ASHP + hybrids
|  | 2020 28: Scenario; 2020 32: Balanced Net Zero Pathway / Widespread Engagement / Headwinds | [10 empty] | Widespread Innovation / Tailwinds Scenarios
|  | 2020 28: Year; 2020 32: 2020; 2020 56: 2030 |  |  |  |  | 2050 | [5 empty] | 2020 | [5 empty] | 2030 | [5 empty] | 2050
|  | 2020 28: Price; 2020 32: CAPEX (£); 2020 48: Marginal (£/kW); 2020 52: Fixed (£); 2020 56: CAPEX (£) |  |  | Marginal (£/kW) | Fixed (£) | CAPEX (£) |  |  |  | Marginal (£/kW) | Fixed (£) | CAPEX (£) |  |  |  | Marginal (£/kW) | Fixed (£) | CAPEX (£) |  |  |  | Marginal (£/kW) | Fixed (£) | CAPEX (£) |  |  |  | Marginal (£/kW) | Fixed (£)
Simple name | Size of system (kW) | Minimum size (kW) | Sizing increments (kW) | OPEX (£/y) | Lifetime (y) Balanced Net Zero Pathway / Widespread Engagement / Headwinds | Lifetime (y) Widespread Innovation / Tailwinds Scenarios | 8 | 12 | 16 | 20 |  |  | 8 | 12 | 16 | 20 |  |  | 8 | 12 | 16 | 20 |  |  | 8 | 12 | 16 | 20 |  |  | 8 | 12 | 16 | 20 |  |  | 8 | 12 | 16 | 20 |  |  | Assumptions | Source
ASHP | ASHP unit cost + fittings + controls + labour (excludes buffer tank/cylinder and heat distribution system) | 4 | 1 | 103.8666 | 15 | 17 | 7250 | 9000 | 10550 | 11675 | 370.625 | 4430 | 5800 | 7200 | 8440 | 9340 | 296.5 | 3544 | 5075 | 6300 | 7385 | 8172.5 | 259.4375 | 3101 | 7250 | 9000 | 10550 | 11675 | 370.625 | 4430 | 5075 | 6300 | 7385 | 8172.5 | 259.4375 | 3101 | 4350 | 5400 | 6330 | 7005 | 222.375 | 2658 | "High" cost applied for 16 kW systems and larger (as is done in the source itself). 20% reduction in ASHP capex from 2020 to 2030 in the Balanced Net Zero Pathway / Widespread Engagement / Headwinds scenarios. 30% reduction in ASHP capex from 2020 to 2050 in the Balanced Net Zero Pathway / Widespread Engagement / Headwinds scenarios. 30% reduction in ASHP capex from 2020 to 2030 in the Widespread Innovation / Tailwinds scenarios. 40% reduction in ASHP capex from 2020 to 2050 in the Widespread Innovation / Tailwinds scenarios. Values used in the model are those under the denoted "fixed" and "marginal" costs. These costs are derived from the raw capex data (cost of specific sizes) based on a linear relationship of best fit. Raw data may not exactly match the relationship derived. | Costs: The Cost of Installing Heating Measures in Domestic Properties, Delta-EE for BEIS (2018) Cost reduction based on stakeholder feedback (see below). Feedback ranges from 25-35%. Published evidence suggests 20%: https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/498962/150113_Delta-ee_Final_ASHP_report_DECC.pdf Lifetime: European Commission (2017), Technical Study on the Macroeconomics of Energy and Climate Policies: https://ec.europa.eu/energy/sites/ener/files/documents/technical_analysis_residential_heat.pdf Danish Energy Energy (energistyrelsen): https://ens.dk/sites/ens.dk/files/Analyser/technologydatafor_heating_installations_marts_2018.xlsx Further evidence of ASHP Lifetimes from ASHRAE: https://www.naturalhandyman.com/iip/infhvac/ASHRAE_Chart_HVAC_Life_Expectancy.pdf Lifetime and cost reductions in each scenario based on feedback from heat pump stakeholders. Opex: Opex assumptions aligned to Fifth Carbon Budget (flat rate opex assumed across non-hybrid technologies).
High T ASHP | High temperature ASHP unit cost + fittings + controls + labour (excludes buffer tank/cylinder and heat distribution system) | 4 | 1 | 103.8666 | 15 | 17 | 7975 | 9900 | 11605 | 12842.5 | 407.6875 | 4873 | 6380 | 7920 | 9284 | 10274 | 326.15 | 3898.4 | 5582.5 | 6930 | 8123.5 | 8989.75 | 285.3812 | 3411.1 | 7975 | 9900 | 11605 | 12842.5 | 407.6875 | 4873 | 5075 | 6300 | 7385 | 8172.5 | 259.4375 | 3101 | 4350 | 5400 | 6330 | 7005 | 222.375 | 2658 | High temp. heat pump is one that is operating at a designed temp. above 60C (no cost premium for those designed to operate at 60C or below). Assume opex and lifetime are the same as a standard ASHP (see sources for ASHP). Assume a 10% capex price premium (on the fully installed cost) compared to a standard ASHP) no premium in the Innovation/Tailwinds scenarios. Values used in the model are those under the denoted "fixed" and "marginal" costs. These costs are derived from the raw capex data (cost of specific sizes) based on a linear relationship of best fit. Raw data may not exactly match the relationship derived. | Price Premium: https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/565248/Heat_Pumps_Combined_Summary_report_-_FINAL.pdf This source indicates a price premium based on fully installed costs is ~10-20%. Based on feedback from heat pump stakeholders, 10% was chosen for modelling. However, it should be noted that some expert external stakeholders viewed this as a potentially pessimistic foward-looking assumption.
Communal ASHP | Communal ASHP (large centralised ASHP with ambient loop to smaller individual HPs in the dwellings) | 2020 12: 4; 2020 15: 1; 2020 18: 103.8666; 2020 24: 15; 2020 28: 17; 2020 48: 583.75 |  |  | 467 | [5 empty] | 408.625 | [5 empty] | 583.75 | [5 empty] | 408.625 | [5 empty] | 350.25 |  | Opex is assumed to be the same as an individual ASHP considering the configuration; marginal capex is based on largest individual heat pump size (20kW) data point. Configuration: Large centralised ASHP which supplies the ambient loop at 25C. Small individual HPs in each dwelling which boost the temperature to 50C for SH and 60C for HW. Marginal capex based on taking the largest system cost (based on Delta EE data) to determine the £/kW (£11,675 for a 20 kW system). The development of these costs have been tested with external heat pump stakeholders;they are at the lower bound of the range suggested. Additional communal costs (e.g. piping) are not included in the values shown here; they are availablein the 'Additional costs' tab (under Communal heating costs). | Typical configuration could have 10 flats (based on English Housing Survey 2017-2018) MHCLG Internal analysis, English Housing Survey, 2018 dwelling sample Configuration based on an ambient loop design: https://cpd.building.co.uk/courses/cpd-1-2020-ambient-loop-carbon-zero/. There are known to be a range of possible configurations for Communal systems.
Hybrid ASHP + hydrogen boiler | Hybrid heat pump (Hyready boiler in Gas mode or hydrogen mode) Includes ASHP unit cost + boiler unit cost + fittings + controls + labour (excludes buffer tank/cylinder and heat distribution system) | 4 | 1 | 157.7333 | 15 | 16 | 8756.0661 | 10506.0661 | 12056.0661 | 13181.0661 | 370.625 | 5936.0661 | 7306.0661 | 8706.0661 | 9946.0661 | 10846.0661 | 296.5 | 5050.0661 | 6581.0661 | 7806.0661 | 8891.0661 | 9678.5661 | 259.4375 | 4607.0661 | 8756.0661 | 10506.0661 | 12056.0661 | 13181.0661 | 370.625 | 5936.0661 | 6581.0661 | 7806.0661 | 8891.0661 | 9678.5661 | 259.4375 | 4607.0661 | 5856.0661 | 6906.0661 | 7836.0661 | 8511.0661 | 222.375 | 4164.0661 | Boiler cost £1050, control unit cost £300. £100 added for Hyready boiler. Opex assumed to be £50 lower than the sum of the opex for the two components of the hybrid system (£104 each) due to economies of scale; no further uplift based on findings that pre-mixed combustion of hydrogen (i.e. in domestic boilers) is typically lower NOX than natural gas. (Costs converted from 2017 values to 2019). Values used in the model are those under the denoted "fixed" and "marginal" costs. These costs are derived from the raw capex data (cost of specific sizes) based on a linear relationship of best fit. Raw data may not exactly match the relationship derived. | 2020 values from Hybrid Heat Pumps (2017), Element Energy for BEIS https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/700572/Hybrid_heat_pumps_Final_report-.pdf Boiler cost based on 24kW boiler from: The Cost of Installing Heating Measures in Domestic Properties, Delta-EE for BEIS (2018) Increase in capex for Hyready boiler in line with Hydrogen supply chain evidence base report, Element Energy for BEIS (2018)
Hybrid ASHP + bio boiler | Hybrid heat pump (Bio boiler) Includes ASHP unit cost + boiler unit cost + fittings + controls + labour (excludes buffer tank/cylinder and heat distribution system) | 4 | 1 | 222.7333 | 15 | 16 | 9192.306 | 10942.306 | 12492.306 | 13617.306 | 370.625 | 6372.306 | 7742.306 | 9142.306 | 10382.306 | 11282.306 | 296.5 | 5486.306 | 7017.306 | 8242.306 | 9327.306 | 10114.806 | 259.4375 | 5043.306 | 9192.306 | 10942.306 | 12492.306 | 13617.306 | 370.625 | 6372.306 | 7017.306 | 8242.306 | 9327.306 | 10114.806 | 259.4375 | 5043.306 | 6292.306 | 7342.306 | 8272.306 | 8947.306 | 222.375 | 4600.306 | Boiler cost £1570, control unit cost £300. Opex assumed to be £50 lower than the sum of the opex for the two components of the hybrid system due to economies of scale with £65 added to opex to reflect delivery and storage of gas. (Costs converted from 2017 values to 2019). Costs include removal of old components, new cost, fittings, control, and labour. Values used in the model are those under the denoted "fixed" and "marginal" costs. These costs are derived from the raw capex data (cost of specific sizes) based on a linear relationship of best fit. Raw data may not exactly match the relationship derived. BioLPG fuel costs have been used on a representative basis and should not be taken to indicate a recommendation on a particular biofuel solution. | Costs of an oil boiler have been used to represent the capex for the boiler component of the system (£1570) based on 24kW boiler from: The Cost of Installing Heating Measures in Domestic Properties, Delta-EE for BEIS (2018). Range of boilers here are are assumed to have similar costs: https://www.boilerguide.co.uk/articles/lpg-boiler-guide-pros-cons-costs (UK boiler guide data with estimated boiler capex ranges from several manufacturers) and https://www.theheatinghub.co.uk/lpg-boiler-installation-fuel-tank-costs (estimate of combi boiler capex from industry professionals) https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/831069/Bioenergy_heating_options_in_off-gas_grid_homes.pdf (NFFCC study for BEIS with estimates of installation costs) £65 added to opex to reflect delivery and storage of gas, based on https://householdquotes.co.uk/lpg-gas-central-heating-costs/ (accessed 25/02/2019)
Hybrid ASHP + resistive heating | Hybrid heat pump with resistive heating Includes ASHP unit cost + resistive heating unit cost + fittings + controls + labour (excludes buffer tank/cylinder and heat distribution system) | 4 | 1 | 157.7333 | 15 | 17 | 7797.3771 | 9547.3771 | 11097.3771 | 12222.3771 | 487.9943 | 4977.3771 | 6347.3771 | 7747.3771 | 8987.3771 | 9887.3771 | 413.8693 | 4091.3771 | 5622.3771 | 6847.3771 | 7932.3771 | 8719.8771 | 376.8068 | 3648.3771 | 7797.3771 | 9547.3771 | 11097.3771 | 12222.3771 | 487.9943 | 4977.3771 | 5622.3771 | 6847.3771 | 7932.3771 | 8719.8771 | 376.8068 | 3648.3771 | 4897.3771 | 5947.3771 | 6877.3771 | 7552.3771 | 339.7443 | 3205.3771 | Control unit cost £300. Values used in the model are those under the denoted "fixed" and "marginal" costs. These costs are derived from the raw capex data (cost of specific sizes) based on a linear relationship of best fit. Raw data may not exactly match the relationship derived. Opex assumed to be £50 lower than the sum of the opex for the two components of the hybrid system (£104 each) due to economies of scale. | Costs derived by removing boiler component of hybrid heat pump and adding cost of resistive heating based on modelled kW (resistive element) per kW (heat pump)
GSHP
|  | 2020 28: Scenario; 2020 32: Balanced Net Zero Pathway / Widespread Engagement / Headwinds | [10 empty] | Widespread Innovation / Tailwinds Scenarios
|  | 2020 28: Year; 2020 32: 2020; 2020 56: 2030 |  |  |  |  | 2050 | [5 empty] | 2020 | [5 empty] | 2030 | [5 empty] | 2050
|  | 2020 28: Price; 2020 32: CAPEX (£); 2020 48: Marginal (£/kW); 2020 52: Fixed (£); 2020 56: CAPEX (£) |  |  | Marginal (£/kW) | Fixed (£) | CAPEX (£) |  |  |  | Marginal (£/kW) | Fixed (£) | CAPEX (£) |  |  |  | Marginal (£/kW) | Fixed (£) | CAPEX (£) |  |  |  | Marginal (£/kW) | Fixed (£) | CAPEX (£) |  |  |  | Marginal (£/kW) | Fixed (£)
Simple name | Size of system (kW) | Minimum size (kW) | Sizing increments (kW) | OPEX (£/y) | Lifetime (y) Balanced Net Zero Pathway / Widespread Engagement / Headwinds | Lifetime (y) Widespread Innovation / Tailwinds Scenarios | 8 | 12 | 16 | 20 |  |  | 8 | 12 | 16 | 20 |  |  | 8 | 12 | 16 | 20 |  |  | 8 | 12 | 16 | 20 |  |  | 8 | 12 | 16 | 20 |  |  | 8 | 12 | 16 | 20 |  |  | Assumptions | Source
GSHP | GSHP unit cost + fittings + controls + labour (excludes buffer tank/cylinder and heat distribution system) Fixed and marginal capex noted include groundworks. | 4 | 1 | 103.8666 | 20 | 22 | 11700 | 12350 | 15500 | 16800 | 531.25 | 9070 | 9360 | 9880 | 12400 | 13440 | 418 | 7112 | 8190 | 8645 | 10850 | 11760 | 371.875 | 6349 | 11700 | 12350 | 15500 | 16800 | 531.25 | 9070 | 8190 | 8645 | 10850 | 11760 | 364.875 | 6205 | 7020 | 7410 | 9300 | 10080 | 318.75 | 5442 | "High" cost applied for 16 kW systems and larger (as is done in the source itself) 20% reduction in GSHP capex from 2020 to 2030 in the Balanced Net Zero Pathway / Widespread Engagement / Headwinds scenarios. 30% reduction in GSHP capex from 2020 to 2050 in the Balanced Net Zero Pathway / Widespread Engagement / Headwinds scenarios. 30% reduction in GSHP capex from 2020 to 2030 in the Widespread Innovation / Tailwinds scenarios. 40% reduction in GSHP capex from 2020 to 2050 in the Widespread Innovation / Tailwinds scenarios. Values used in the model are those under the denoted "fixed" and "marginal" costs. These costs are derived from the raw capex data (cost of specific sizes) based on a linear relationship of best fit. Raw data may not exactly match the relationship derived. | Costs: The Cost of Installing Heating Measures in Domestic Properties, Delta-EE for BEIS (2018) Lifetime: European Commission (2017), Technical Study on the Macroeconomics of Energy and Climate Policies: https://ec.europa.eu/energy/sites/ener/files/documents/technical_analysis_residential_heat.pdf Danish Energy Energy (energistyrelsen): https://ens.dk/sites/ens.dk/files/Analyser/technologydatafor_heating_installations_marts_2018.xlsx Lifetime and cost reduction in scenarios based on feedback from heat pump stakeholders. Opex: Opex assumptions aligned to Fifth Carbon Budget (flat rate opex assumed across non-hybrid technologies).
High T GSHP | High temperature GSHP unit cost + fittings + controls + labour (excludes buffer tank/cylinder and heat distribution system) Fixed and marginal capex noted include groundworks. | 4 | 1 | 103.8666 | 20 | 22 | 12870 | 13585 | 17050 | 18480 | 584.375 | 9977 | 10296 | 10868 | 13640 | 14784 | 459.8 | 7823.2 | 9009 | 9509.5 | 11935 | 12936 | 409.0625 | 6983.9 | 12870 | 13585 | 17050 | 18480 | 584.375 | 9977 | 8190 | 8645 | 10850 | 11760 | 364.875 | 6205 | 7020 | 7410 | 9300 | 10080 | 318.75 | 5442 | High temp. heat pump is one that is operating at a designed temp. above 60C (no cost premium for those designed to operate at 60C or below). Assume opex and lifetime are the same as a standard GSHP (see sources for GSHP). Assume a 10% capex price premium (on the fully installed cost) compared to a standard GSHP); no premium in the innovation/Tailwinds scenarios. Values used in the model are those under the denoted "fixed" and "marginal" costs. These costs are derived from the raw capex data (cost of specific sizes) based on a linear relationship of best fit. Raw data may not exactly match the relationship derived. | Price Premium: https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/565248/Heat_Pumps_Combined_Summary_report_-_FINAL.pdf This source indicates a price premium based on fully installed costs is ~10-20%. Based on feedback from heat pump stakeholders, 10% was chosen for modelling. However, it should be noted that some expert external stakeholders viewed this as a potentially pessimistic foward-looking assumption.
Communal GSHP | Communal GSHP (large centralised GSHP with ambient loop to smaller individual HPs in the dwellings; shared ground loop) | 2020 12: 4; 2020 15: 1; 2020 18: 103.8666; 2020 24: 20; 2020 28: 22; 2020 48: 976 |  |  | 767.2 | [5 empty] | 683.2 | [5 empty] | 976 | [5 empty] | 669.6 | [5 empty] | 585.6 |  | Opex is same as for individual GSHP considering the configuration. Configuration: Large centralised GSHP which supplies the ambient loop at 25C. Small individual HPs in each dwelling which boost the temperature to 50C for SH and 60C for HW. Marginal capex based on taking the largest system cost (based on Delta EE data) to determine the £/kW. Additional communal costs (e.g. piping) are not included in the values shown here; they are availabel in the 'Additional costs' tab (under Communal heating costs). | Typical configuration could have 10 flats (based on from English Housing Survey 2017-2018) MHCLG Internal analysis, English Housing Survey, 2018 dwelling sample Limited feedback was received via external stakeholder engagement and there are known to be a range of possible configurations for communal systems. This can be considered a potential area for future further research.
Hybrid GSHP + hydrogen | Hybrid heat pump (Hyready boiler in Gas mode or hydrogen mode) Includes GSHP unit cost + boiler unit cost + fittings + controls + labour (excludes buffer tank/cylinder and heat distribution system) Fixed and marginal capex noted include groundworks. | 4 | 1 | 157.7333 | 19 | 20 | 13206.0661 | 13856.0661 | 17006.0661 | 18306.0661 | 531.25 | 10576.0661 | 10866.0661 | 11386.0661 | 13906.0661 | 14946.0661 | 418 | 8618.0661 | 9696.0661 | 10151.0661 | 12356.0661 | 13266.0661 | 371.875 | 7855.0661 | 13206.0661 | 13856.0661 | 17006.0661 | 18306.0661 | 531.25 | 10576.0661 | 9696.0661 | 10151.0661 | 12356.0661 | 13266.0661 | 364.875 | 7711.0661 | 8526.0661 | 8916.0661 | 10806.0661 | 11586.0661 | 318.75 | 6948.0661 | Boiler cost £1050, control unit cost £300. £100 added for Hyready boiler. Opex assumed to be £50 lower than the sum of the opex for the two components of the hybrid system (£104 each) due to economies of scale; no further uplift based on findings that pre-mixed combustion of hydrogen (i.e. in domestic boilers) is typically lower NOX than natural gas. (Costs converted from 2017 values to 2019). Values used in the model are those under the denoted "fixed" and "marginal" costs. These costs are derived from the raw capex data (cost of specific sizes) based on a linear relationship of best fit. Raw data may not exactly match the relationship derived. | 2020 values from Hybrid Heat Pumps (2017), Element Energy for BEIS https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/700572/Hybrid_heat_pumps_Final_report-.pdf Boiler cost based on 24kW boiler from: The Cost of Installing Heating Measures in Domestic Properties, Delta-EE for BEIS (2018) Increase in capex for Hyready boiler in line with Hydrogen supply chain evidence base report, Element Energy for BEIS (2018)
Hybrid GSHP + bio boiler | Hybrid heat pump (Bio boiler) Includes GSHP unit cost + boiler unit cost + fittings + controls + labour (excludes buffer tank/cylinder and heat distribution system) Fixed and marginal capex noted include groundworks. | 4 | 1 | 222.7333 | 19 | 20 | 13642.306 | 14292.306 | 17442.306 | 18742.306 | 531.25 | 11012.306 | 11302.306 | 11822.306 | 14342.306 | 15382.306 | 418 | 9054.306 | 10132.306 | 10587.306 | 12792.306 | 13702.306 | 371.875 | 8291.306 | 13642.306 | 14292.306 | 17442.306 | 18742.306 | 531.25 | 11012.306 | 10132.306 | 10587.306 | 12792.306 | 13702.306 | 364.875 | 8147.306 | 8962.306 | 9352.306 | 11242.306 | 12022.306 | 318.75 | 7384.306 | Boiler cost £1570, control unit cost £300. Opex assumed to be £50 lower than the sum of the opex for the two components of the hybrid system due to economies of scale with £65 added to opex to reflect delivery and storage of gas. (Costs converted from 2017 values to 2019). Costs include removal of old components, new cost, fittings, control, and labour. Values used in the model are those under the denoted "fixed" and "marginal" costs. These costs are derived from the raw capex data (cost of specific sizes) based on a linear relationship of best fit. Raw data may not exactly match the relationship derived. BioLPG fuel costs have been used on a representative basis and should not be taken to indicate a recommendation on a particular biofuel solution. | Costs of an oil boiler have been used to represent the capex for the boiler component of the system (£1570) based on 24kW boiler from: The Cost of Installing Heating Measures in Domestic Properties, Delta-EE for BEIS (2018). Range of boilers here are are assumed to have similar costs: https://www.boilerguide.co.uk/articles/lpg-boiler-guide-pros-cons-costs (UK boiler guide data with estimated boiler capex ranges from several manufacturers) and https://www.theheatinghub.co.uk/lpg-boiler-installation-fuel-tank-costs (estimate of combi boiler capex from industry professionals) https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/831069/Bioenergy_heating_options_in_off-gas_grid_homes.pdf (NFFCC study for BEIS with estimates of installation costs) £65 added to opex to reflect delivery and storage of gas, based on https://householdquotes.co.uk/lpg-gas-central-heating-costs/ (accessed 25/02/2019)
Hybrid GSHP + resistive heating | Hybrid heat pump with resistive heating Includes GSHP unit cost + resistive heating unit cost + fittings + controls + labour (excludes buffer tank/cylinder and heat distribution system) Fixed and marginal capex noted include groundworks. | 4 | 1 | 157.7333 | 20 | 22 | 12247.3771 | 12897.3771 | 16047.3771 | 17347.3771 | 648.6193 | 9617.3771 | 9907.3771 | 10427.3771 | 12947.3771 | 13987.3771 | 535.3693 | 7659.3771 | 8737.3771 | 9192.3771 | 11397.3771 | 12307.3771 | 489.2443 | 6896.3771 | 12247.3771 | 12897.3771 | 16047.3771 | 17347.3771 | 648.6193 | 9617.3771 | 8737.3771 | 9192.3771 | 11397.3771 | 12307.3771 | 482.2443 | 6752.3771 | 7567.3771 | 7957.3771 | 9847.3771 | 10627.3771 | 436.1193 | 5989.3771 | Control unit cost £300. Values used in the model are those under the denoted "fixed" and "marginal" costs. These costs are derived from the raw capex data (cost of specific sizes) based on a linear relationship of best fit. Raw data may not exactly match the relationship derived. Opex assumed to be £50 lower than the sum of the opex for the two components of the hybrid system (£104 each) due to economies of scale. | Costs derived by removing boiler component of hybrid heat pump and adding cost of resistive heating based on modelled kW (resistive element) per kW (heat pump)
GSHP (groundworks)
|  | Scenario | Balanced Net Zero Pathway / Widespread Engagement / Headwinds | [7 empty] | Widespread Innovation / Tailwinds Scenarios
|  | 2020 12: Year; 2020 15: 2020; 2020 32: 2030; 2020 48: 2020 | 2030
|  | Price | CAPEX (£) | [7 empty] | CAPEX (£)
Simple name | Size of system (kW) | Lifetime (y) | 8 | 12 | 16 | 20 | 8 | 12 | 16 | 20 | 8 | 12 | 16 | 20 | 8 | 12 | 16 | 20 | Assumptions | [10 empty] | Source
GSHP trench | Trench | 100 | 4000 | 6000 | 8000 | 8000 | 2800 | 4200 | 5600 | 5600 | 4000 | 6000 | 8000 | 8000 | 2400 | 3600 | 4800 | 4800 | Cost of ground collector - trench including installation (with margin). Source suggests using the "Low" cost for 12 kW and less and the "High" cost for 12 kW and above. Here, we have applied "Low" for 8 kW, "Balanced Net Zero Pathway" for 12 kW and "High" for 16 kW and 20 kW to derive a smoother trend with size. 30% reduction of base cost to 2030 for the Balanced Net Zero Pathway / Widespread Engagement / Headwinds scenarios. 40% reduction of base cost to 2030 for Widespread Innovation / Tailwindds scenarios. Values used in the model are those under the denoted "fixed" and "marginal" costs. These costs are derived from the raw capex data (cost of specific sizes) based on a linear relationship of best fit. Raw data may not exactly match the relationship derived. | [10 empty] | Costs: The Cost of Installing Heating Measures in Domestic Properties, Delta-EE for BEIS (2018) Cost reductions based on feedback from external heat pump stakeholders (Mitsubishi Electric UK, Glen Dimplex Heating & Ventilation, Ground Source Heat Pump Association, The Kensa Group, and the Heat Pump Association). Lifetimes: Optimistic, based on mixed review (50+ years to 100+ years from the links below) and validation and feedback from external heat pump stakeholders (Ground Source Heat Pump Association, The Kensa Group). - UK Energy Agency: https://www.energyagency.org.uk/en/ground-source-heat-pump_46650/ - GSHPA: https://www.gshp.org.uk/ground_source_heat_pumps_Domestic.html - Greenmatch: https://www.greenmatch.co.uk/heat-pump/ground-source-heat-pump/ground-source-heat-pump-prices - Plumbing & Heating Contractors: https://ottersouthwest.co.uk/new-ground-source/ 80%/20% split of the blended cost based on feedback frome external stakeholders. Supported by the split between rural/urban of 17%/83% from: https://www.gov.uk/government/publications/rural-population-and-migration/rural-population-201415
GSHP borehole | Borehole | 100 | 11000 | 13000 | 15000 | 15000 | 7700 | 9100 | 10500 | 10500 | 11000 | 13000 | 15000 | 15000 | 6600 | 7800 | 9000 | 9000 | Cost of ground collector - borehole including installation (with margin). Source suggests using the "Low" cost for 12 kW and less and the "High" cost for 12 kW and above. Here, we have applied "Low" for 8 kW, "Balanced Net Zero Pathway" for 12 kW and "High" for 16 kW and 20 kW to derive a smoother trend with size. 30% reduction of base cost to 2030 for the Balanced Net Zero Pathway / Widespread Engagement / Headwinds scenarios. 40% reduction of base cost to 2030 for Widespread Innovation / Tailwinds scenarios. Values used in the model are those under the denoted "fixed" and "marginal" costs. These costs are derived from the raw capex data (cost of specific sizes) based on a linear relationship of best fit. Raw data may not exactly match the relationship derived.
GSHP blended groundworks | Borehole/Trench blended cost | 100 | 9600 | 11600 | 13600 | 13600 | 6720 | 8120 | 9520 | 9520 | 9600 | 11600 | 13600 | 13600 | 5760 | 6960 | 8160 | 8160 | Cost based on a 80%/20% blend of borehole and trench systems. 30% reduction of base cost to 2030 for the Balanced Net Zero Pathway / Widespread Engagement / Headwinds scnearios. 40% reduction of base cost to 2030 for Widespread Innovation / Tailwinds scenarios. Values used in the model are those under the denoted "fixed" and "marginal" costs. These costs are derived from the raw capex data (cost of specific sizes) based on a linear relationship of best fit. Raw data may not exactly match the relationship derived.
Water Softener
CAPEX (£)
| House size | Lifetime | CAPEX (£) 8: Small; CAPEX (£) 12: Medium; CAPEX (£) 16: Large; CAPEX (£) 20: Assumptions; CAPEX (£) 20: Source
| Electronic Water Conditioner | 20 | CAPEX (£) 8: 125; CAPEX (£) 12: 170; CAPEX (£) 16: 230; CAPEX (£) 20: Assumed to be suitable for all house types and locations Cost excluding VAT; CAPEX (£) 20: Scalewatcher Brochure (2012) Available on Amazon today https://www.scalewatcher.co.uk/files/attachments/scalewatcher-brochure.pdf https://www.amazon.co.uk/ScaleWatcher-Electronic-Conditioner-Inhibitor-Prevents/dp/B006H4HIDA https://www.amazon.co.uk/Scalewatcher-SW3-Scale-Watcher-Star/dp/B009T300A4/ref=sr_1_2?keywords=scalewatcher+3+star&qid=1584042091&s=home-garden&sr=1-2 https://www.amazon.co.uk/Scalewatcher-Limescale-Control-1-star/dp/B006H4H3NA/ref=sr_1_3?keywords=scalewatcher+3+star&qid=1584042091&s=home-garden&sr=1-3

## Additional costs
All costs are expressed in a base year of £2019 (converted from the source data where appropriate).
CAPEX (£)
Technology | Building size | 2015 | 2020 | 2030 | 2040 | 2050 | Assumptions |  | Source
Heat battery (6 kWh) | All | 2088.2698 | 1752.2508 | 1080.213 | 1080.213 | 1080.213 | Assume installation cost included within installation cost for the main heating system. Assume heat battery becomes cost-competitive with hot water cylinder by 2030. Converts originally assumed NZ costs to 2019 values. |  | Current cost from: (1) http://www.bublshop.co.uk/sunamp-uniq-e-dual-heating-hot-water-storage/p2040. (2) https://www.cibse.org/getmedia/630ad6ec-ce8b-43c7-9304-04c52b3790fc/Sunamp-Presentation-updated.pdf.aspx
Hot water cylinder | Small | 918.181 | No reduction |  |  |  | Assumes market typical cost for 180L storage. Converts originally assumed NZ costs to 2019 values. Based on BEIS NHM data: 14.6% of oil boilers are combi boilers; all other oil boilers can be assumed to have HW tanks. 50% of gas boilers are combi boilers; all other gas boilers can assumed to have HW tanks. |  | Evidence gathering for electric options in off-gas grid homes (2019) Element Energy for BEIS BEIS NHM data. Costs for a small and large are based on a 15% differential down and up, respectively, against medium. Some evidence for lower costs: HW cylinder costs were suggested by Dr. Richard Hall (Energy Transitions) to be between £500-£1000+ (excl. VAT); link below corroborates https://heatingforce.co.uk/blog/installation-cost-vented-unvented-hot-water-cylinders/
| Medium | 1080.213
| Large | 1242.2449
Buffer tank | Small | 200 |  |  |  |  | Cost of buffer tank and cylinder with margin 50% of new heat pump systems assumed to need buffer tanks in Balanced Net Zero Pathway / Headwinds / Widespread Engagement scenarios. 0% of new heat pump systems assumed to need buffer tanks in Widespread Innovation / Tailwinds scenarios. |  | Feedback from external heat pump stakeholders indicating prices sub £500, averaging £200-£300. Some examples: https://ampair.co.uk/wp-content/uploads/2019/05/UK-A2W-PRICE-LIST-AMP-19-LR.pdf https://www.kensaheatpumps.com/accessory/buffer-tanks/ Additionally, it should be noted that the assumptions for buffer tank requirements are based on mixed views from stakehodlers regarding when/if buffer tanks are needed.
| Medium | 300
| Large | 500
Additional thermal store to allow some use of Off peak electricity for heating | All | 1744.9594 |  |  |  |  | Cost has been derived to be applicable to both heat battery costs and the costs (and storage capacity) associated with two 180L hot water tanks (modelling assumes that most households are able to install the former). Converts originally assumed NZ costs to 2019 values. |  | Evidence gathering for electric options in off-gas grid homes (2019) Element Energy for BEIS
Point-of-use hot water systems | All | 2101.2219 |  |  |  |  | Assumes typical installation of 3 electric taps and 1 electric shower per dwelling (based on average seen in modelling) Converts originally assumed NZ costs to 2019 values. |  | Evidence gathering for electric options in off-gas grid homes (2019) Element Energy for BEIS
Conversion to low T radiators | Small | 1121.7596 |  |  |  |  | Applied in dwellings with existing wet heating system, when existing radiators estimated to be insufficient to supply peak heat demand (suitability calculation). Converts originally assumed NZ costs to 2019 values. |  | Hybrid Heat Pumps (2017), Element Energy for BEIS
| Medium | 1869.5993
| Large | 2617.4391
Replacement of cooker/hob | All | 321.5711 |  |  |  |  | Weighted average across gas households, based on cost of £500 (2017 prices), 23.9m gas households, with 14.8m gas hobs and 8.4m gas ovens. Converts originally assumed NZ costs to 2019 values. |  | Analysis of Alternative UK Heat Decarbonisation Pathways (2018) Imperial College for CCC
Installation and decommissioning costs
Process | Scenario | Fixed CAPEX (£) | Marginal CAPEX† (£/m2) | Assumptions |  |  |  | Source
Installation of wet distribution system | Small | 1038.6663 | 4.1547 | Only applied in dwellings with electric incumbent system when switching to wet heating system Converts originally assumed NZ costs to 2019 values. |  |  |  | Evidence gathering for electric options in off-gas grid homes (2019) Element Energy for BEIS
| Medium | 1298.3329 | 5.1933
| Large | 1557.9995 | 6.232
Removal of wet heating system | Best | 103.8666 |  | Only applied in dwellings with non-electric incumbent system when switching to electric or storage heating Converts originally assumed NZ costs to 2019 values. |  |  |  | Evidence gathering for electric options in off-gas grid homes (2019) Element Energy for BEIS
| Central | 207.7333
| Worst | 311.5999
Decommissioning of boiler | All | 519.3332 |  | Includes decommissioning of other non-cooking gas appliances Converts originally assumed NZ costs to 2019 values. |  |  |  | Analysis of Alternative UK Heat Decarbonisation Pathways (2018) Imperial College for CCC
H2 conversion costs - hydrogen boiler and hydrogen hybrid heat pump | All | 571.2665 |  | £509 for pipework. For Hyready boiler (not Hydrogen-only boiler) £51 added as additional 1 hour labour cost associated with the switchover of the Hyready boiler from gas to hydrogen. Converts originally assumed NZ costs to 2019 values. |  |  |  | Pipework costs: Hydrogen supply chain evidence base (2018) Element Energy for BEIS (slide 89) Labour cost: Hydrogen supply chain evidence base (2018) Element Energy for BEIS (slide 89, assuming £50/hour labour cost)
Communal heating costs
Process | House type | Fixed CAPEX (£) | Marginal CAPEX† (£/m2) | Assumptions |  |  |  | Source
Additional pipework for communal heat pump (excluding internal emitter replacement which may also be required) | Flat | 2848.2536 | - | Includes: Heat exchange unit and meter (£1901 per house/flat, 2017 prices) Flats: 2.5m service pipe per flat, 10m lateral pipe and 3.1m heat riser per floor (total £2652.75 per 10 flats), building pump (total £90.52 per 10 flats) and installation and labour costs (£5668.95 per 10 flats) Terraces: 30m external pipeline per communal heating system (£16,578 per 6 houses) and 2.5m service pipe per house (£1381 per house), including installation and trenching Converts originally assumed NZ costs to 2019 values. |  |  |  | Element Energy modelling for private sector client (2018) Assumption of 10 flats per low-rise building based on: MHCLG Internal analysis, English Housing Survey, 2018 dwelling sample
| Terrace | 6279.361 | -
†based on floor area of property
Additional wiring and installation costs applied when switching from non-electric to electric heating:
Technology | Scenario | Fixed | Marginal (£/kW) | Assumptions |  |  |  | Source
Electric heating | Balanced Net Zero Pathway | 90.364 | 138.1426 | Only applied in dwellings with non-electric incumbent system when switching to electric heating. Converts originally assumed NZ costs to 2019 values. |  |  |  | Evidence gathering for electric options in off-gas grid homes (2019) Element Energy for BEIS
Storage heating | Balanced Net Zero Pathway | 519.3332 | 181.7666 | Applied in dwellings with non-storage heating incumbent system when switching to storage heating. Converts originally assumed NZ costs to 2019 values. |  |  |  | Evidence gathering for electric options in off-gas grid homes (2019) Element Energy for BEIS

## Efficiencies
Scenario | Balanced Net Zero Pathway | Headwinds | Widespread Engagement / Widespread Innovation / Tailwinds
Technology | Load factor (factor applied to annual space heating demand to estimate peak heating need for calculating the system size - used purely for determining the size of the unit; not necessarily an estimate of the proportion of time it is running) |  |  | Heating efficiency (higher heating value for combustion-based technologies) | % space heating demand | % hot water demand | Source / Comments
Gas boiler | 5% | 5% | 5% | 87% | 100% | 100% | Efficiencies in-line with Fifth Carbon Budget. Load factor based on BEIS feedback.
Oil boiler | 9% | 9% | 9% | 84% | 100% | 100% | Efficiencies in-line with Fifth Carbon Budget. Load factor based on BEIS feedback suggesting oil boilers are typically sized smaller than gas boilers due to most not being combi boilers. Blended load factor derived using gas boiler load factor for combi oil boilers and electric resistive load factor for normal oil boilers. Electric resistive used as a proxy for normal oil boilers as assumed to be the closest system (system with hot water cylinder, hence baseload-dominated operating mode, but less uniform demand profile than for a HP). Using the 85%/15% split of normal/combi oil boilers (based on BEIS NHM data) gives a blended load factor for oil boilers of 1/((1/5%)*.15+(1/11%)*.85) = 9%.
Bio boiler | 9% | 9% | 9% | 84% | 100% | 100% | Efficiencies in-line with Fifth Carbon Budget. Load factor aligned to that of an oil boiler (based on BEIS feedback).
Hydrogen boiler (Hydrogen-only and Hyready boiler) | 5% | 5% | 5% | 80% | 100% | 100% | Efficiency based on BEIS, via NIST Chemistry WebBook. Hydrogen boilers have the same efficiency as gas boilers at lower heating value (LHV) and it is the conversion to high heating value (HHV) that give sthe lower efficiency. Value based on fundamental physical properties, not actual test results for hydrogen boilers. Load factor based on BEIS feedback to match gas boiler load factors.
Electric resistive heating | 11% | 11% | 11% | 100% | 100% | 100% | Efficiencies and load factors in-line with Fifth Carbon Budget.
Storage heater | 16% | 16% | 16% | 100% | 100% | 100% | Efficiencies and load factors in-line with Fifth Carbon Budget.
ASHP | 20.5% | 16% | 25% | See below | 100% | 100% | Scenarios with point-of-use systems will assume no hot water demand met by heat pump. Load factor based on BEIS NHM data for Widespread Engagement, Widespread Innovation and Tailwinds; based on 5CB for Headwinds, based on an average of the two values for Balanced Net Zero Pathway.
GSHP | 20.5% | 16% | 25% | See below | 100% | 100% | Scenarios with point-of-use systems will assume no hot water demand met by heat pump. Load factor based on BEIS NHM data for Widespread Engagement, Widespread Innovation and Tailwinds; based on 5CB for Headwinds, based on an average of the two values for Balanced Net Zero Pathway.
Hybrid heat pump - boiler (no HW storage) | 31.25% | 25% | 37.5% | 87% | 20% | 100%
Hybrid heat pump - heat pump (no HW storage) |  |  |  | See below | 80% | 0% | Assume heat pump SPF same as ASHP for ASHP hybrids and same as GSHP for GSHP hybrids, assuming a flow temperature of 40°C (based on the average flow temperature seen in our Balanced Net Zero Pathway for deployed heat pumps); assume boiler not used to top up flow temperature (HP and boiler not used in series). Load factor based on Element Energy analysis.
Hybrid heat pump - boiler (with HW storage) |  |  |  | 87% | 20% | 20%
Hybrid heat pump - heat pump (with HW storage) |  |  |  | See below | 80% | 80% | Assume heat pump SPF same as ASHP for ASHP hybrids and same as GSHP for GSHP hybrids, assuming a flow temperature of 40°C; assume boiler not used to top up flow temperature (HP and boiler not used in series). Load factor based on Element Energy analysis.
Solar thermal (configuration 1) | N/A | N/A | N/A |  | 0% | 60% | 60% of the hot water demand is assumed to be delivered by solar thermal where installed (remaining 40% met by the heating system), based on (Table B.13 of NERA/AEA, The UK Supply Curve for Renewable Heat, 2009. Link: https://webarchive.nationalarchives.gov.uk/20101209162908/http://www.decc.gov.uk/assets/decc/What%20we%20do/UK%20energy%20supply/Energy%20mix/Renewable%20energy/Renewable%20Energy%20Strategy/1_20090715120507_e_@@_NERAAEATheUKSupplyCurveforRenewableHeaturn09689.pdf)
Solar thermal (configuration 2) | N/A | N/A | N/A |  | 50% | 60% | Evidence provided by Dr Richard Hall (Energy Transitions) suggests solar thermal can contribute to 60% of hot water demand and 50% of space heating demand with remaining gaps met by the heating system.
Hybrid heat pump + resistive - heat pump | 31.25% | 25% | 37.5% | See below | 80% | 80% | Assume heat pump SPF same as ASHP assuming a flow temperature of 40°C. Load factor based on Element Energy analysis.
Hybrid heat pump + resistive - resistive heating |  |  |  | 100% | 20% | 20%
|  | Space heating SPF | Space heating SPF | Hot water SPF (60C) | Hot water SPF (60C) | Combined SPF assuming space heat:hot water ratio of 3.5:1 (Balanced Net Zero Pathway/Headwinds/Widespread Engagement Scenarios) |  | Combined SPF assuming space heat:hot water ratio of 3.5:1 (Innovation/Tailwinds Scenarios - HaaS)
Technology | Flow Temperature (°C) | 2020 | 2030 | 2020 | 2030 | 2020 | 2030 | 2020 | 2030 | Comments
ASHP | 35 | 3.6 | 4.056 |  |  | 3.1199 | 3.6194 | 3.5879 | 4.1623 | Assumptions on heat pump efficiencies are based on alignment with the Fifth Carbon Budget, with a 2.54 combined efficiency being assumed for a heat pump operating at a 50 degree flow temperature in 2020. The MCS Emitter Guide (referenced below) has been used to infer what efficiency gains might be realised where there are substantial radiator upgrades that allow operation at lower temps. Efficiences were tested with external expert stakeholders prior to finalising. 2020 Space heating SPF values for the full range of flow temperatures (column D) taken from MCS Emitters Guide (https://www.microgenerationcertification.org/images/MIS_3005_Supplementary_Information_2_-_Heat_Emitter_Guide_v2.0_Print_Version.pdf, Accessed 01/02/2019) The hot water SPF is assumed to be that of the highest space heating flow temperature (60°C). Individual space heating and hot water SPFs were calculated from the combined SPF assuming space heating:hot water demand ratio of 3.5 and setting the hot water SPF to be that of the highest space heating flow temperature (60°C). An improvement of 0.5 in the combined SPF is assumed by 2030, in-line with 5CB. In the Widespread Engagement scenario, HPs operate at 50C for their HW - with one hour a day at 60C to allow for a legionella cycle - to reflect the savings (via efficienncy gains) of the behavioural measure of using water at a lower temperature. 15% increase in efficeincy in the innovation scenario (based on external stakeholder feedback).
| 40 | 3.4 | 3.8668 |  |  | 2.9999 | 3.4995 | 3.4499 | 4.0244
| 45 | 3 | 3.484 |  |  | 2.7464 | 3.2462 | 3.1584 | 3.7331
| 50 | 2.7 | 3.1928 |  |  | 2.5435 | 3.0433 | 2.925 | 3.4998
| 55 | 2.4 | 2.8982 |  |  | 2.3283 | 2.8283 | 2.6776 | 3.2526
| 60 | 2.1 | 2.6 | 2.1 | 2.6 | 2.1 | 2.6 | 2.415 | 2.99
| 65 | 1.8375 | 2.275 |  |  | 1.8375 | 2.275 | 2.1131 | 2.6163 | Decrease of 25% in performance from 60C to 70C; 65C taken as the average between 60C and 70C Corroborated by the relative decrease between a standard T heat pump and high T heat pump (~25%) from: https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/762596/Technical_Feasibility_of_Electric_Heating_in_Rural_Off-Gas_Grid_Dwellings.pdf 15% increase in efficeincy in the innovation scenario (based on external stakeholder feedback).
| 70 | 1.575 | 1.95 |  |  | 1.575 | 1.95 | 1.8113 | 2.2425
GSHP | 35 | 3.7611 | 4.2354 |  |  | 3.3719 | 3.8716 | 3.8777 | 4.4523 | Assumptions on heat pump efficiencies are based on alignment with the Fifth Carbon Budget, with a 2.84 combined efficiency being assumed for a heat pump operating at a 50 degree flow temp in 2020. The MCS Emitters Guide (referenced below) has been used to infer what efficiency gains might be realised where there are substantial radiator upgrades that allow operation at lower temps. Efficiences were tested with external expert stakeholders prior to finalising. 2020 Space heating SPF values for the full range of flow temperatures (column D) taken from MCS Emitters Guide (https://www.microgenerationcertification.org/images/MIS_3005_Supplementary_Information_2_-_Heat_Emitter_Guide_v2.0_Print_Version.pdf, Accessed 01/02/2019) The hot water SPF is assumed to be that of the highest space heating flow temperature (60°C). Individual space heating and hot water SPFs were calculated from the combined SPF assuming space heating:hot water demand ratio of 3.5 and setting the hot water SPF to be that of the highest space heating flow temperature (60°C). An improvement of 0.5 in the combined SPF is assumed by 2030, in-line with 5CB. 15% increase in efficeincy in the innovation scenario (based on external stakeholder feedback). In the Widespread Engagement scenario, HPs operate at 50C for their HW - with one hour a day at 60C to allow for a legionella cycle - to reflect the savings (via efficienncy gains) of the behavioural measure of using water at a lower temperature.
| 40 | 3.5862 | 4.0668 |  |  | 3.2601 | 3.7598 | 3.7491 | 4.3238
| 45 | 3.2363 | 3.727 |  |  | 3.0267 | 3.5266 | 3.4807 | 4.0556
| 50 | 2.9739 | 3.4697 |  |  | 2.8427 | 3.3426 | 3.2691 | 3.844
| 55 | 2.7115 | 3.2104 |  |  | 2.6503 | 3.1503 | 3.0479 | 3.6228
| 60 | 2.4491 | 2.9491 | 2.4491 | 2.9491 | 2.4491 | 2.9491 | 2.8164 | 3.3914
| 65 | 2.1429 | 2.5804 |  |  | 2.1429 | 2.5804 | 2.4644 | 2.9675 | Decrease of 25% in performance from 60C to 70C; 65C taken as the average between 60C and 70C Corroborated by the relative decrease between a standard T heat pump and high T heat pump (~25%) from: https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/762596/Technical_Feasibility_of_Electric_Heating_in_Rural_Off-Gas_Grid_Dwellings.pdf 15% increase in efficeincy in the innovation scenario (based on external stakeholder feedback)
| 70 | 1.8368 | 2.2118 |  |  | 1.8368 | 2.2118 | 2.1123 | 2.5436
Communal ASHP | 35 | 6 | 6.7166 |  |  | 5.4 | 6.0974 | 6.21 | 7.0121 | Communal ASHP efficiencies are a weighted average between the the large centralised heat pump providing the ambient loop at 25C and the smaller individual heat pump in the dwelling providing the heating/HW. Centralised heat pump (10C-->25C) Individual heat pump (25C-->required temperature) Communal configuration based on Daikin Ambient loop system design and corroborated by other external heat pump stakeholders.
| 40 | 5.4 | 6.084 |  |  | 4.9333 | 5.6054 | 5.6733 | 6.4462
| 45 | 4.7143 | 5.3844 |  |  | 4.4 | 5.0613 | 5.06 | 5.8205
| 50 | 4.2 | 4.8557 |  |  | 4 | 4.6501 | 4.6 | 5.3476
| 55 | 3.7333 | 4.3763 |  |  | 3.637 | 4.2772 | 4.1826 | 4.9188
| 60 | 3.3 | 3.9303 | 3.3 | 3.9303 | 3.3 | 3.9303 | 3.795 | 4.5199
| 65 | 2.9284 | 3.4844 |  |  | 3.011 | 3.5835 | 3.4626 | 4.121
| 70 | 2.575 | 3.0586 |  |  | 2.7361 | 3.2523 | 3.1465 | 3.7402
Communal GSHP | 35 | 6.2277 | 6.9789 |  |  | 5.5771 | 6.3015 | 6.4136 | 7.2467 | Communal GSHP efficiencies are a weighted average between the the large centralised heat pump providing the ambient loop at 25C and the smaller individual heat pump in the dwelling providing the heating/HW. Centralised heat pump (10C-->25C) Individual heat pump (25C-->required temp) Communal configuration based on Daikin Ambient loop system design and corroborated by other external heat pump stakeholders. Limited feedbak was received via external stakeholder engagement regarding GSHPs. This can be considered a potential area for future further research.
| 40 | 5.6416 | 6.3531 |  |  | 5.1213 | 5.8147 | 5.8895 | 6.6869
| 45 | 4.9981 | 5.6866 |  |  | 4.6208 | 5.2963 | 5.3139 | 6.0908
| 50 | 4.5155 | 5.1844 |  |  | 4.2454 | 4.9057 | 4.8822 | 5.6416
| 55 | 4.0818 | 4.7346 |  |  | 3.9081 | 4.5559 | 4.4943 | 5.2393
| 60 | 3.6824 | 4.3209 | 3.6824 | 4.3209 | 3.5974 | 4.2341 | 4.137 | 4.8692
| 65 | 3.2641 | 3.8275 |  |  | 3.2721 | 3.8504 | 3.7629 | 4.4279
| 70 | 2.8646 | 3.355 |  |  | 2.9613 | 3.4828 | 3.4055 | 4.0052
Source: MCS Emitter Guide
Flow temperature will be chosen for each archetype based on heating demand and appropriate emitter oversizing, with lowest possible flow temperature favoured.
i.e. The model does not assume a standard input flow temperature for a heat pump. Rather, this is determined based on the archetype-specific factors such as the demand, floor area, heat loss factor, etc. From this, the required peak temperature is chosen and then the corresponding SPF is extracted from the above table. It is assumed that this SPF includes the seasonal COP variation. However, there is uncertainty on whether this is only capturing COP changes due to outside temperature or also lower flow temperature, as this is not specified in the Emitter Guide (i.e. the SPF given in the Emitter Guide is a seasonal efficiency rather than the efficiency at the peak period; but it is not specified whether this assumes that a lower flow temperature is used away from peak periods). If not, this would mean the SPF could be higher than specified if a variable flow temperature is used.

## Suitability matrices
Unsuitable for all dwellings
Sutiable for some dwellings under specified conditions
Suitable for all dwellings
Technology suitability matrix
[6 empty] | Scenario | Balanced Net Zero Pathway / Headwinds / Widespread Innovation | Widespread Engagement / Tailwinds
| W/m2 constraint (heat supply temperature constraint applicable to low temperature emitters) | Fuse limit (applicable to all electrical heating technologies) | Dwelling type |  |  |  | Space constraint (Total floor area divide number habitable rooms) |  |  | Gas grid |  | Heat density | Heritage status
Heating systems |  |  | Detached | Semi-detached | Terrace | Flat | <16m2 | <16m2 | >16m2 | Connected | Not connected | <30kWh/m2 | Conservation area | Grade I | Grade II* | Grade II | Comments | Source
ASHP/High T ASHP - hot water cylinder serving DHW only or thermal store to allow off-peak space heating | Up to 150 W/m2 peak demand | Fuse limit | [10 empty] | 50% of Detached, Semi-detached and Terraces suitable, no Flats suitable |  |  |  | Suitability of heating systems deemed to require higher levels of space in homes has been constrained for the portion of the stock modelled as having internal space constraints. This includes systems which require a hot water tank, thermal store or multiple internal units. GSHPs are modelled as having higher suitability in space constrained homes relative to ASHPs. This reflects feedback from assumptions testing, and is intended to reflect greater potential for configurations where key components are positioned outside.Space requirements can be reduced where a heat battery (or point of use hot water system) is used rather than a hot water tank, and this is reflected in higher suitability for these configurations. There remains uncertainty over the number of smaller homes that would be willing to accept the space required even by a heat battery and we therefore limit suitability, while testing higher acceptance levels in Widespread Engagement and Tailwinds. Assumptions about the ratio of boreholes vs trenches for GSHP groundworks intended to partially reflect some of the impacts of external space limitations. There remain a range of factors which would be expected to impact suitability but which it has not been possible to include in this modelling. Beyond assumptions over the proportion of boreholes and trenches, it has not been possible in this work to model the impact of external space constraints on suitability. Other constraints not modelled, but which would be expected to have an impact, include geological suitability, noise impacts and exposure. As for Net Zero analysis, assume that homes designated as having some form of heritage status could have additional suitability constraints as a result of required permissions. These constraints remain a function of policy, rather than technical suitability which is considered separately and summarised in the preceeding columns. Listed buildings have special protection and require consent for changes in materials, details and finishes, both internally and externally. Buildings in conservation areas may require permission to make changes to the external appearance of the building. For these reasons, suitability of heating technologies with requirement for external modifications (including heat pumps and hybrids which require an external unit; and solar thermal) is limited to reflect the potential to find a suitable location to host the external unit in each case. In addition, solar thermal suitability is set to 0% in Grade I listed buildings given the additional restrictions and high visibility of this system. Air Source Heat Pumps and hybrids are not deemed suitable for heritage buildings that are also flats, given the additional challenges in finding suitable locations to host the external unit. Higher suitability of GSHPs in heritage homes reflects feedback from assumptions testing that GSHPs generally enable less obtrusive solutions - this also leads to greater suitability for GSHPs in flats relative to ASHPs. In line with feedback from heritage professionals all individual heat pump configurations are assumed to have some limitations on suitability. Whilst not modelled, biomass heating may also be subject to restrictions as it typically requires a larger flue. It is important to note that all assumptions relating to space constraint and heritage suitability are highly uncertain, and the assumptions used in this modelling remain a first step in examining a subset of potential constraints. In relation to homes designated as having some form of heritage status, any constraints will be highly specific to the building in question and its reason for listing or conservation classification. All assumptions are for the purposes of an illustrative representation of potential constraints in the modelling only, and should not be interpreted as guidance for retrofit in homes. | Assignments based on literature recommendations (see sources below) and refined in consultation with retrofit and heat pump experts. A wide variety of views were received which undelines the high levels of uncertainty associated with these assumptions. Retrofitting Historic Buildings for Sustainability (2013) City of Westminster http://transact.westminster.gov.uk/docstores/publications_store/Retrofitting_Historic_Buildings_for_Sustainability_January_2013.pdf Energy Efficiency & Renewable Energy Guidance For Listed Buildings and Undesignated Buildings (2013) Bath & North East Somerset Council Heat demand limit assumptions taken from MCS Emitters Guide (https://www.microgenerationcertification.org/images/MIS_3005_Supplementary_Information_2_-_Heat_Emitter_Guide_v2.0_Print_Version.pdf, Accessed 01/02/2019). A level of uncertainty exists in this assumption; in reality the suitability will vary with conventional vs high T HPs.
ASHP/High T ASHP - small heat battery serving DHW only | [6 empty] | 50% of dwellings suitable | 75% of dwellings suitable
GSHP/High T GSHP - hot water cylinder serving DHW only or thermal store to allow off-peak space heating | [12 empty] | 75% of Detached, Semi-detached and Terraces suitable
GSHP/High T GSHP - small heat battery serving DHW only | [6 empty] | 75% of dwellings suitable; all systems to use boreholes (not trenches) | All systems to use boreholes (not trenches)
Hybrid ASHP (on-gas, with gas/hydrogen boiler) - no hot water cylinder | [6 empty] | 50% of dwellings suitable | 75% of dwellings suitable |  |  |  |  | 50% of Detached, Semi-detached and Terraces suitable, no Flats suitable
Hybrid ASHP (on-gas, with gas/hydrogen boiler) - hot water cylinder
Hybrid ASHP (off-gas, with biofuel boiler) - no hot water cylinder | [6 empty] | 50% of dwellings suitable | 75% of dwellings suitable
Hybrid ASHP (off-gas, with biofuel boiler) - hot water cylinder
Hybrid ASHP with resistive heating | [6 empty] | Small heat battery (for DHW) | Small heat battery (for DHW)
Hybrid GSHP (on-gas, with gas/hydrogen boiler) - no hot water cylinder | [6 empty] | 75% of dwellings suitable | [5 empty] | 75% of Detached, Semi-detached and Terraces suitable
Hybrid GSHP (on-gas, with gas/hydrogen boiler) - hot water cylinder
Hybrid GSHP (off-gas, with biofuel boiler) - no hot water cylinder | [6 empty] | 75% of dwellings suitable
Hybrid GSHP (off-gas, with biofuel boiler) - hot water cylinder
Hybrid GSHP with resistive heating | [6 empty] | Small heat battery (for DHW) | Small heat battery (for DHW)
Communal ASHP - hot water cylinder serving DHW only or thermal store to allow off-peak space heating | Up to 150 W/m2 peak demand | Fuse limit
Communal ASHP - small heat battery serving DHW only | Up to 150 W/m2 peak demand | Fuse limit
Communal GSHP - hot water cylinder serving DHW only or thermal store to allow off-peak space heating | Up to 150 W/m2 peak demand | Fuse limit
Communal GSHP - small heat battery serving DHW only | Up to 150 W/m2 peak demand | Fuse limit
Electric resistive heating (including with solar thermal) - thermal store to allow off-peak space heating |  | Fuse limit
Electric resistive heating (including with solar thermal) |  | Fuse limit |  |  |  |  | Small heat battery (for DHW) | Small heat battery (for DHW)
Storage heating |  | Fuse limit
Heat network
Hydrogen boiler
Solar thermal | [12 empty] | 50% of dwellings suitable |  | 50% of dwellings suitable | 50% of dwellings suitable
Energy efficiency measure suitability matrix
Balanced Net Zero Pathway assumptions
| Efficiency measures (N.B. Any packages containing an unsuitable measure are deemed unsuitable) | [5 empty] | Heritage status |  |  |  | Comments | [5 empty] | Source
Wall Insulation | Internal Wall Insulation | [5 empty] | 50% of dwellings suitable |  |  |  | While the suitability matrix reflects some generalised feedback on the extent to which measures are currently considered suitable for different types of property in the context of current planning and consent limitations, the variability in the heritage sector necessitates that every building is considered on a case-by-case basis and would generally require a bespoke assessment and recommendations. All assumptions are for the purposes of an illustrative representation of potential constraints in the modelling only, and should not be interpreted as guidance for retrofit in homes. Assumptions here have been updated to reflect feedback from a survey of heritage professionals undertaken by UCL. For more discussion see UCL for the CCC (2020) Analysis work to refine fabric energy efficiency assumptions for use in developing the Sixth Carbon Budget. Relative to the Net Zero analysis, a simplified approach has been taken whereby all homes designated as having heritage status are subject to the same suitability constraints. The revised suitability approach is expected to lead to a pessimistic assessment for a portion of homes. Nevertheless it is important to note that the overall representation of heritage constraints in the modelling is likely to lead to an optimistic assessment of suitability overall, due to the fact that some of the limitations that apply to listed homes and homes in conservation areas would be expected to apply to traditional buildings more widely - generally considered to be those built prior to 1919. This work reflects only a high-level illustration of the potential current impacts of planning permission and listed buildings consent, and does not reflect the wider considerations which apply to traditional buildings. Evidence remains extremely limited and research on decarbonisation approaches for traditional buildings is an important area for further work. | [5 empty] | UCL for the CCC (2020) Analysis work to refine fabric energy efficiency assumptions for use in developing the Sixth Carbon Budget, drawing on a survey of a range of built environment professionals . Assessment also informed by previous analysis to inform the Net Zero advice, drawing on: Retrofitting Historic Buildings for Sustainability (2013) City of Westminster http://transact.westminster.gov.uk/docstores/publications_store/Retrofitting_Historic_Buildings_for_Sustainability_January_2013.pdf Energy Efficiency & Renewable Energy Guidance For Listed Buildings and Undesignated Buildings (2013) Bath & North East Somerset Council
| Cavity Wall Insulation | [5 empty] | 50% of dwellings suitable
External Wall Insulation
Windows | Secondary glazing | [5 empty] | 50% of dwellings suitable
| Replace with double-glazed | [5 empty] | 50% of dwellings suitable
Doors | Proofing
Replacement
Loft Insulation | Top-up to 300mm where partial insulation present
Replacement
Ground floor insulation | Under floor insulation | [5 empty] | 50% of dwellings suitable

## Application of additional costs
|  |  |  | Assumed for/cost applied to all dwellings |  |  |  |  | Assumed for/cost applied to some dwellings | [6 empty] | Assumption does not apply for/cost not applied to any dwellings
Application of additional capex costs
|  |  | Assumptions about new system |  |  |  | Assumptions about existing heating system | [5 empty] | Costs applied
| New system | Existing system | Wet heating system required | Communal distribution system required | Hot water solution required | Low temperature system | Existing wet heating system present | Existing communal distribution system present | Existing wiring suitable for storage heaters present | Existing wiring suitable for resistive heaters present | Existing hot water tank present | Existing non-gas cooker/hob present | Removal of wet system | Installation of wet system | Communal heating pipework and meter | Storage heating electrical wiring | Resistive heating electrical wiring | Hot water tank/thermal storage | Heat battery | Radiator upgrades | Decommission boiler and non-cooking gas appliances | Decommission/replace cooking appliances | Hydrogen pipework and conversion
| ASHP/GSHP inc. option with solar thermal | Gas | [8 empty] | [8] | [1] | [5 empty] | [8] | [2] | [3] |  | [1]
|  | Oil | [8 empty] | [8] | [6 empty] | [8] | [2] | [3]
|  | Electric resistive | [17 empty] | [3]
|  | Electric storage | [17 empty] | [3]
|  | Community | [16 empty] | [2] | [3]
| Communal ASHP/GSHP | Gas | [8 empty] | [8] | [1] | [5 empty] | [8] | [2] | [3] |  | [1]
|  | Oil | [8 empty] | [8] | [6 empty] | [8] | [2] | [3]
|  | Electric resistive | [17 empty] | [3]
|  | Electric storage | [17 empty] | [3]
|  | Community | [16 empty] | [2] | [3]
| Electric (resistive) inc. option with solar thermal | Gas | [8 empty] | [8] | [1] | [5 empty] | [8] | [4] |  |  | [1]
|  | Oil | [8 empty] | [8] | [6 empty] | [8] | [4]
Electric resistive
Electric storage
|  | Community | [16 empty] | [4]
| Storage heating inc. option with solar thermal | Gas | [8 empty] | [8] | [1] | [5 empty] | [8] | [4] |  |  | [1]
|  | Oil | [8 empty] | [8] | [6 empty] | [8] | [4]
Electric resistive
Electric storage
|  | Community | [16 empty] | [4]
| Hybrid heat pump All options | Gas |  |  | [5] | [5 empty] | [8] | [1] | [5 empty] | [5] | [4] |  |  |  | [6]
|  | Oil | [8 empty] | [8] | [6 empty] | [5] | [4] |  |  |  | [6]
|  | Electric resistive | [20 empty] | [6]
|  | Electric storage | [20 empty] | [6]
|  | Community | [15 empty] | [5] | [4] |  |  |  | [6]
| Hydrogen | Gas | [8 empty] | [8] | [1] | [9 empty] | [1]
|  | Oil | [8 empty] | [8]
Electric resistive
Electric storage
Community
| Low carbon heat networks | Gas | [8 empty] | [8] | [1] |  |  | [9] |  |  |  |  | [3] |  | [1]
|  | Oil | [8 empty] | [8] |  |  |  | [9] |  |  |  |  | [3]
|  | Electric resistive | [12 empty] | [9] |  |  |  |  | [3]
|  | Electric storage | [12 empty] | [9] |  |  |  |  | [3]
|  | Community | [12 empty] | [9] |  |  |  |  | [3]
| Biomass | Gas | [8 empty] | [8] | [1] | [8 empty] | [7] | [1]
|  | Oil | [8 empty] | [8]
Electric resistive
Electric storage
Community
[1] Assume that 62% of gas households have a gas hob and 35% have a gas oven (in line with assumptions in Analysis of Alternative UK Heat decarbonisation Pathways (2018) Imperial College, from ECUK 2017 data); a weighted average cost is applied to all gas households assuming £500 conversion cost for either hob, oven, or hob and oven replacement, and assuming all households with a gas oven also have a gas hob.
[2] Where heat battery required (i.e. space constrained homes), applied instead of a conventional hot water tank. Additionally, in the Widespread Innovation scenario, it is assumed that heat batteries are the standard over conventional hot water tanks.
[3] Applied when standard radiators are deemed to be insufficient to supply peak heat demand, based on an assumed oversizing factor for standard radiators of 1.3: if (1.3 x baseline space heating demand) divided by (required oversize factor x energy demand after energy efficiency) is less than 1 then radiator upgrades are required. The required oversize factor is determined by the flow temperature of the system; the model aims to optimise for operation at the lowest possible flow temperature.
[4] Small heat battery for domestic hot water is an option to provide on-demand hot water where a combi boiler is not available (or not used) to provide hot water in space constrained homes. This is therefore applied in space-constrained homes assumed not to have a hot water cylinder. Additionally, in the Widespread Innovation scenario, it is assumed that heat batteries are the standard over conventional hot water tanks. In reality, Point-of-Use electrical hot water systems may also be an option for typical consumers.
[5] Only applicable in options where the heat pump is meeting the hot water demand (where the boiler is meeting hot water demand then on-demand hot water from a combi boiler is assumed).
[6] Applicable in on-gas hybrids only.
[7] Cost is applied in the model but suitability assumptions do not allow biomass boilers in on-gas homes therefore this cost is not applied in practice.
[8] Based on BEIS NHM data (2014), 50% of gas boilers are combi boilers and 15% of oil boilers are combi boilers; each proportion of non-combi boilers is assumed to have an existing hot water tank present. As such, costs (when required) are only applicable in 50% of the cases for gas boilers and 85% of the cases for oil boilers.
[9] Communal heating pipework and metering is costed implicitly as part of the deployment of low carbon heat networks.

## Heritage cost uplifts
Low carbon heating cost uplift
|  | Cost uplift - Low |  |  |  | Cost uplift - Balanced Net Zero Pathway |  |  |  | Cost uplift - High
| Heating systems | Conservation area | Grade I | Grade II* | Grade II | Conservation area | Grade I | Grade II* | Grade II | Conservation area | Grade I | Grade II* | Grade II | Basis |  |  |  | Source
| ASHP - hot water cylinder serving DHW only or thermal store to allow off-peak space heating | 25% uplift in cost of emitters |  |  |  | 50% uplift in cost of emitters |  |  |  | 75% uplift in cost of emitters |  |  |  | As for the analysis for Net Zero, we assume an increase in cost of 25-75% is associated with emitters of more appropriate aesthetic value than standard emitters. Views gathered from a small sample of manufactuers and heritage professionals indicate that there are likely to be additional costs for installing low carbon heat in traditional homes, above and beyond the cost of heat emitters, including: - Additional protection to conserve the fabric of the building during works - The costs associated with hiding systems from view - Other costs associated with bespoke apporaches required to preserve the character of the building - Archeological surveys Limited evidence is available to quantify this, and on this basis cost uplifts have been modelled conservatively, only applying to the cost of heat emitters. |  |  |  | Consultation with retrofit experts (including heat pump manufacturers and heritage professionals)
ASHP - small heat battery serving DHW only
GSHP (shared ground loop) - hot water cylinder serving DHW only
GSHP (shared ground loop) - small heat battery serving DHW only
GSHP (shared ground loop) - additional thermal store to allow off-peak space heating
| Hybrid HP - no hot water cylinder | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% |  |  |  |  | Consultation with retrofit experts (including heat pump manufacturers and heritage professionals)
| Hybrid HP - hot water cylinder | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Hybrid HP (off-gas) - no hot water cylinder | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Hybrid HP (off-gas) - hot water cylinder | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Hybrid HP with resistive heating | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Communal ASHP | 25% uplift in cost of emitters |  |  |  | 50% uplift in cost of emitters |  |  |  | 75% uplift in cost of emitters |  |  |  | See above
| Communal GSHP | [12 empty] | See above
| Electric resistive heating | 25% uplift in cost of emitters |  |  |  | 50% uplift in cost of emitters |  |  |  | 75% uplift in cost of emitters |  |  |  | See above
Storage heating
| Heat network | 25% uplift in cost of emitters |  |  |  | 50% uplift in cost of emitters |  |  |  | 75% uplift in cost of emitters |  |  |  | See above
| Hydrogen boiler | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | No uplift in cost is expected for boiler technology
| Biomass boiler | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0%
| Solar thermal | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | 0% | Where solar thermal is suitable, the installed system is the same for heritage homes as for standard homes - no increase in cost incurred
Energy efficiency measures cost uplift
| Overall package cost uplift | Cost uplift - Low |  |  |  | Cost uplift - Medium |  |  |  | Cost uplift - High
| Package type | Conservation area | Grade I | Grade II* | Grade II | Conservation area | Grade I | Grade II* | Grade II | Conservation area | Grade I | Grade II* | Grade II
| Low | 24.8% | 24.8% | 24.8% | 24.8% | 186.3% | 186.3% | 186.3% | 186.3% | 416.9% | 416.9% | 416.9% | 416.9%
| Medium | 20.11% | 20.11% | 20.11% | 20.11% | 176.8% | 176.8% | 176.8% | 176.8% | 315.1% | 315.1% | 315.1% | 315.1%
| High | 21.96% | 21.96% | 21.96% | 21.96% | 186.2% | 186.2% | 186.2% | 186.2% | 348% | 348% | 348% | 348%
| Cost uplift per measure | Walls |  |  | Double glazing |  |  | Secondary glazing |  |  | Loft |  |  | Floor |  |  | Other
| Heritage status | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High
| Conservation | 30% | 220% | 500% | 50% | 80% | 300% | 50% | 100% | 300% | 5% | 70% | 110% | 15% | 170% | 200% | 0% | 0% | 0%
| Heritage | 30% | 220% | 500% | 50% | 80% | 300% | 50% | 100% | 300% | 5% | 70% | 110% | 15% | 170% | 200% | 0% | 0% | 0%
| Basis | Cost assumptions, relative to Net Zero have been updated to a) take into account additional evidence based on UCL modelling for Bath and North East Somerset Council and b) to model on a simplified basis, assuming uniform cost uplifts across all listed and conservation area homes. Revised costing based primarily on UCL modelling of three archetype traditional homes for Bath & North East Somerset Council, with supplementary evidence used from Retrofit for the Future to derive ranges. Evidence remains very limited and is an important area for futher research.
| Source | UCL modelling for Bath & North East Somerset Council (2013) Retrofitting Estimate Spreadsheet. - UCL modelling does not take into account various initiatives by government, energy companies and others to install energy saving measures such as roof insulation. Prices quoted for such works are subject to special offers, cross subsidy and other pricing distortions and cannot be relied upon to be available at all times. - The costings in the UCL modelling are based on a series of standard model buildings. Costs for actual buildings will vary according to size, nature, location, orientation and condition. - The costings in the UCL modelling assume that the building to be treated is in good structural order with all relevant maintenance routines up to date For further discussion see UCL for the CCC (2020) Analysis work to refine fabric energy efficiency assumptions for use in developing the Sixth Carbon Budget. Evidence base supplemented with, Retrofit for the Future: analysis of cost data (2014) and Retrofit for the Future case studies
|  | Wall |  |  | Window |  |  | Loft |  |  | Floor |  |  | Other
|  | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High | Low | Medium | High
| Average contribution of measure to package cost across building stock archetypes | 80.5% | 43.5% | 52.8% | 0% | 0% | 0% | 13.1% | 8.2% | 5.6% | 0% | 44.3% | 38.9% | 6.4% | 4% | 2.7%
| Basis | Energy Efficiency Package Savings v41: Average contribution of each measure to total package cost across building archetypes
| Source | Calculated based on results of UCL energy efficiency modelling

## Scenario assumptions
Scenario assumptions
Scenarios
|  | Single-theme |  |  | Hybrids
| Innovation area | Widespread Engagement | Widespread Innovation | Headwinds | Balanced Net Zero Pathway | Tailwinds
Building fabric | Energy efficiency packages and deployment - fuel poor | High packages for all fuel poor homes. | High packages for all fuel poor homes. | High packages for all fuel poor homes. | High packages for all fuel poor homes. | High packages for all fuel poor homes.
| Energy efficiency packages and deployment - non-fuel poor | All homes receive at least a medium package (except a subset of heritage homes where a Medium package is unsuitable). | Model permitted to deploy energy efficiency on basis of lowest lifetime cost of package of energy efficiency and low carbon heat. No wider benefits costed. | Model permitted to deploy energy efficiency on basis of lowest lifetime cost of package of energy efficiency and low carbon heat, with higher bound hydrogen prices assumed. No wider benefits costed. | Inclusion of full economic potential for low regret measures including loft and cavity wall insulation. Solid walls deployed where part of a package with a cost effectiveness of <£600/t. | Full economic potential deployed.
| Adjustments to measure assumptions | Base costs and savings | Lower bound costs for all low and medium packages. TIWI (thin IWI) replaces IWI in packages. All high packages assumed to deliver heat demand of 40kWh/m2/yr, with associated costs of high packages uplifted to reflect evidence on potential for cost reduction in deep retrofits (Green Alliance, Reinventing retrofit; discussions with Energiesprong, discussions with retrofit experts). | Base costs and savings | Base costs and savings | Lower bound for low, medium, and high packages.
| Space constraints | Higher suitability of some technologies in space constrained homes (see suitability tab) | Base assumptions | Base assumptions | Base assumptions | Higher suitability of some technologies in space constrained homes (see suitability tab)
| Performance gap | Uplift equivalent to one third closure of in-use factors | Uplift equivalent to one half closure of in-use factors | Uplift equivalent to one third closure of in-use factors | Uplift equivalent to one third closure of in-use factors | Uplift equivalent to one half closure of in-use factors
Heating system | Low-carbon heating restrictions | The following technology restrictions were applied: Fully electrified. No high temperature heat pumps. Biofuels not used. All resistive heating accompanied by thermal storage or solar thermal. | The following technology restrictions were applied: Hydrogen only permitted in hybrid heat pump systems. Biofuels not used. All resistive heating accompanied by thermal storage or solar thermal. | The following technology restrictions were applied: No high temperature heat pumps. Homes in south use hydrogen hybrids and homes in north use hydrogen boilers based on Imperial (2018) Analysis of alternative UK heat decarbonisation pathways, Hybrid - H2 North scenario. Biofuels restricted to use in off-gas hybrids. All resistive heating to be accompanied by thermal storage or solar thermal. | The following technology restrictions were applied: Hydrogen only permitted in hybrid heat pump systems. No high temperature heat pumps. Biofuels restricted to use in off-gas hybrids. All resistive heating to be accompanied by thermal storage or solar thermal. | The following technology restrictions were applied: No high temperature heat pumps. Biofuels not used. All resistive heating to be accompanied by thermal storage or solar thermal. Hydrogen boilers deployed around industrial clusters.
| Buffer tanks required with heat pumps | 50% of time | Never | 50% of time | 50% of the time | Never
| Heat pump lifetimes | 15yrs for ASHPs, 20yrs for GSHPs | 17yrs for ASHPs, 22yrs for GSHPs | 15yrs for ASHPs, 20yrs for GSHPs | 15yrs for ASHPs, 20yrs for GSHPs | 17yrs for ASHPs, 22yrs for GSHPs
| GSHP cost savings | 20% to 2030, 30% of 2050 | 30% to 2030; 40% to 2050 | 20% to 2030, 30% of 2050 | 20% to 2030, 30% of 2050 | 30% to 2030; 40% to 2050
| GSHP groundworks | 30% cost reduction to 2030 | 40% cost reduction to 2030 | 30% cost reduction to 2030 | 30% cost reduction to 2030 | 40% cost reduction to 2030
| ASHP cost savings | 20% to 2030, 30% of 2050 | 30% to 2030; 40% to 2050 | 20% to 2030, 30% of 2050 | 20% to 2030, 30% of 2050 | 30% to 2030; 40% to 2050
| Load factors | Aligned with BEIS inputs on technology sizing | Aligned with BEIS inputs on technology sizing | Aligned with BEIS inputs on technology sizing for boilers. Net zero load factors retained for heat pumps. | Aligned with BEIS inputs on technology sizing for boilers. Average of net zero and BEIS load factors for heat pumps. | Aligned with BEIS inputs on technology sizing
| Thermal storage | Deployed where cost-effective | Forced for all non-flexible homes | Deployed where cost-effective | Deployed where cost-effective | Deployed where cost-effective
| Hy-ready boilers | All boiler replacements from 2026 are hyready. Cost at point of conversion. Ensure accounting for scrappage as needed. | All boiler replacements from 2026 are hyready. Cost at point of conversion. Ensure accounting for scrappage as needed. | All boiler replacements from 2026 are hyready. Cost at point of conversion. Ensure accounting for scrappage as needed. | All boiler replacements from 2026 are hyready. Cost at point of conversion. Ensure accounting for scrappage as needed. | All boiler replacements from 2026 are hyready. Cost at point of conversion. Ensure accounting for scrappage as needed.
| District heating mix | Fully electrified (dominated by water- and sewage-source heat pumps) alongside waste heat from industrial sources | Fully electrified (dominated by water- and sewage-source heat pumps) alongside waste heat from industrial sources | As other scenarios, but includes gas peaking which transitions to hydrogen over time. | Fully electrified (dominated by water- and sewage-source heat pumps) alongside waste heat from industrial sources | Fully electrified (dominated by water- and sewage-source heat pumps) alongside waste heat from industrial sources
Behaviour change | Pre-heating | 50% of post-1952 homes | 50% of post-1952 homes | 25% of post 1952 homes | 25% of post 1952 homes | 50% of post-1952 homes
| Reduction in space heat demand from smarter heating management and use | 6% | 6% | 3% | 3% | 6%
| Water temperature | 50 degree water temperature in heat pump homes, with allowance for daily legonella cycle of 1hr duration. | 60 degrees | 60 degrees | 60 degrees | 60 degrees
| Low flow shower head | Yes | Yes | Yes | Yes | Yes
| Heat as a service | No (3.5% cost of capital) | Yes (7.5% cost of capital) | No (3.5% cost of capital) | No (3.5% cost of capital) | Yes (7.5% cost of capital)
Deployment profile | Backstop date by which sufficient energy efficiency required across all eligible homes | Private Rented Sector: 2027 | Private Rented Sector: 2028 | Private Rented Sector: 2030 | Private Rented Sector: 2028 | Private Rented Sector: 2027
|  | Social homes: 2027 | Social homes:2028 | Social homes: 2030 | Social homes: 2028 | Social homes: 2027
| Period over which lenders expected to incentivise retrofits | Owner occupiers (mortgagors): 2025-2030 | Owner occupiers (mortgagors): 2025-2035 | Owner occupiers (mortgagors): 2025-2035 | Owner occupiers (mortgagors): 2025-2033 | Owner occupiers (mortgagors): 2025-2030
| Date by which regulations at trigger points are implemented | Owner occupiers (outright owners): 2025 | Owner occupiers (outright owners): 2030 | Owner occupiers (outright owners): 2030 | Owner occupiers (outright owners): 2028 | Owner occupiers (outright owners): 2025
| Date by which all new heating systems must be low carbon (outside of areas designated for district heat or hydrogen conversion) | Phase out of high carbon fossil boilers: 2026 | Phase out of high carbon fossil boilers: 2028 | Phase out of high carbon fossil boilers: 2028 | Phase out of high carbon fossil boilers: 2028 | Phase out of high carbon fossil boilers: 2026
|  | Phase out of gas boilers: 2030 | Phase out of gas boilers: 2035 | Phase out of gas boilers: 2035 alongside full region by region conversion from 2030 | Phase out of gas boilers: 2033 | Phase out of gas boilers: 2030
| Whole house* vs incremental** deployment | Whole house deployment in social homes only. All other homes subject to incremental deployment. | Whole house deployment in social homes only. All other homes subject to incremental deployment. | All homes subject to incremental deployment. | Whole house deployment in social homes only. All other homes subject to incremental deployment. | Whole house deployment in social homes only. All other homes subject to incremental deployment.
| Rate of fossil heating replacement | After the date by which new fossil installations are phased out, rate of fossil heating system replacement set at 1/13.8 reflecting evidence that 13% of people would consider replacing their heating system whilst it is still working. BEIS (2019) BEIS Public Attitudes Tracker (December 2019, Wave 32, UK) . | After the date by which new fossil installations are phased out, rate of fossil heating system replacement set at 1/13.8 reflecting evidence that 13% of people would consider replacing their heating system whilst it is still working. BEIS (2019) BEIS Public Attitudes Tracker (December 2019, Wave 32, UK) . | 1/15 as per boiler lifetime assumptions. | 1/15 as per boiler lifetime assumptions. | After the date by which new fossil installations are phased out, rate of fossil heating system replacement set at 1/13.8 reflecting evidence that 13% of people would consider replacing their heating system whilst it is still working. BEIS (2019) BEIS Public Attitudes Tracker (December 2019, Wave 32, UK) .
* Whole house deployment is assumed to be where all energy efficiency measures are deployed together.
** Incremental deployment refers to the incremental deployment of energy efficiency measures over time. Where deployment approach is on incremental basis, modelling assumes all measures are deployed such that the full package of energy efficiency in the home is reached by the time the trigger point is met.
Technology / Energy efficiency measure deployment constraints
| Technology group | Limit on annual deployment | [8 empty] | Sources
|  | Easily achievable |  |  | Achievable at a stretch |  |  | Absolute limit
|  | By 2025 | By 2030 | By 2035 | By 2025 | By 2030 | By 2035 | By 2025 | By 2030 | By 2035
| Energy efficiency – lofts | 300000 | 1000000 | 2000000 | 2000000 | 2000000 | 2000000 | 2000000 | 2000000 | 2000000 | Deployment to 2025: based on historical peak annual deployment achieved under ECO since 2015. Source: Hard to Decarbonise Homes, Element Energy for the CCC (2019). Future deployment (2025-2050): based on increasing potential; assumptions derived from the peaks seen under CERT/CESP. Technical potential for loft insulation is 13 million. In the Absolute limit, it is assumed that all the remaining potential is achieved by 2030. All numbers have gone through numerous rounds of expert stakeholder feedback from organisations in the relevant field.
| Energy efficiency – cavity walls | 300000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | 1000000 | Deployment to 2025: based on historical peak annual deployment achieved under ECO since 2015. Future deployment (2025-2050): based on increasing potential; assumptions derived from the peaks seen under CERT/CESP. Technical potential for cavity wall insulation is 6 million. In the Absolute limit, it is assumed that all the remaining potential is achieved by 2030. All numbers have gone through numerous rounds of expert stakeholder feedback from organisations in the relevant field.
| Energy efficiency – solid walls | 80000 | 150000 | 300000 | 240000 | 720000 | 1000000 | 700000 | 1000000 | 1000000 | Deployment to 2025: based on historical peak annual deployment achieved under ECO since 2015. Achievable at a stretch value based on ramping up by a factor of up to 3 from ECO peak. Future deployment (2025-2050): based on increasing potential; Achievable at a Stretch in 2030 value based on ramping up by a factor of up to 3 from 2025 value i.e. by a factor of up to 9 from ECO peak. Technical potential for solid wall insulation is 7 million. In the Absolute limit, it is assumed that all the remaining potential is achieved by 2030. All numbers have gone through numerous rounds of expert stakeholder feedback from organisations in the relevant field.
| Heat pumps (inc. hybrids) | 250000 | 820000 | 1480000 | 450000 | 1320000 | 2080000 | 450000 | 1320000 | 2080000 | Deployment to 2025: Easily achievable roughly reflects the HPA's A Roadmap for the Role of Heat Pumps (2019). Achievable at a stretch roughly reflects the HPA trajectory for new build and assumes a similar number for existing buildings. Future deployment (2025-2050): based on increasing potential; assumptions derived from HPA trajectory. Achievable at a stretch and Absolute limit set at equal levels. Numbers refined based on input from external stakeholders (HPA & GSHPA) in addition to numerous rounds of expert stakeholder feedback.
| Conventional electric heating | 150000 | 500000 | 2000000 | 500000 | 1000000 | 2000000 | 1000000 | 2000000 | 2000000 | Deployment to 2025: based on doubling of deployment rate, derived from current total stock. Source: Hard to Decarbonise Homes, Element Energy for the CCC (2019). Future deployment (2025-2050): based on increasing potential; lower numbers are multiples of estimated current deployment; higher numbers assume full market share. All numbers have gone through numerous rounds of expert stakeholder feedback from organisations in the relevant field.
| Solar thermal | 2000 | 20000 | 200000 | 20000 | 200000 | 1000000 | 100000 | 1000000 | 1000000 | Deployment to 2025: based on multiples of peak annual deployment achieved under RHI. Future deployment (2025-2050): based on increasing potential, peaking at being installed in around half of homes; assumptions derived from the peak seen under RHI. All numbers have gone through numerous rounds of expert stakeholder feedback from organisations in the relevant field.
| Hydrogen / Hyready boilers | 20000 | 1000000 | 1000000 | 1500000 | 2000000 | 1500000 | 2000000 | 2000000 | 2000000 | Based on consultation with industry, suggesting that major boiler manufacturers could respond to a rapid market switch given sufficient notice and in the presence of a hard regulatory signal. Given a rapid switch to Hyready boilers and the highly developed gas installer sector, a full switch to Hyready boilers is assumed achievable by 2030. All numbers have gone through numerous rounds of expert stakeholder feedback from organisations in the relevant field.
| Biofuel boilers | 15000 | 30000 | 75000 | 75000 | 150000 | 150000 | 150000 | 150000 | 150000 | Deployment to 2025: Easily achievable based on assuming 25% of all homes currently using LPG can convert to Bio LPG. Achievable at a stretch based on assuming 50% of all off-grid fossil homes can move to biofuels. Future deployment (2025-2050): based on increasing potential, assuming a clear policy signal to remove all high carbon fossil fuels from off-gas homes by 2030. All numbers have gone through numerous rounds of expert stakeholder feedback from organisations in the relevant field.

## Energy efficiency
Package Formulation
Category | Measure | Building Feature | Short Name | Low | Medium | High |  | * N.B. In the Balanced Net Zero Pathway and Tailwinds scenarios, per the scenario guidance, modelling steps were performed to include the uptake of all lofts / cavities (including hard to treat cavities and lofts).
Solid wall | External (solid) wall insulation | Solid uninsulated (external) | ESWI |  |  | 1
Solid wall | Internal (solid) wall insulation | Solid uninsulated (internal) | ISWI |  | 1 | 1
Solid wall | Thin internal (solid) wall insulation | Solid uninsulated (internal) | TSWI
Cavity wall | Easy to treat cavities (Unfilled) | Cavity uninsulated ETT | ETT CWI | 1 | 1 | 1
Cavity wall | Hard to treat cavities (Unfilled) | Cavity uninsulated HTT | HTT CWI | * | 1 | 1
Roof | Loft insulation | Less than 100mm ETT | ETT loft insulation | 1 | 1 | 1
Roof | Loft insulation | 100 -199mm ETT | ETT loft insulation | 1 | 1 | 1
Roof | Loft insulation (HTT) | Less than 100mm HTT | HTT loft insulation | 1 | 1 | 1
Roof | Loft insulation (HTT) | 100 -199mm HTT | HTT loft insulation | * | 1 | 1
Floor | Suspended timber floor insulation | Suspended uninsulated | Suspended timber floor insulation |  | 1 | 1
Floor | Solid floor insulation | Solid uninsulated | Solid floor insulation |  |  | 1
Glazing | Double glazing (From Band G) | Single glazed | Double glazing (from single glazed)
Glazing | Double glazing (From Band E) | Double glazed pre 2002 | Double glazing (from double glazed pre 2002)
Other | Insulated doors | Insulated doors | Doors
Other | Draught proofing (draught stripping) | Draught proofing (draught stripping) | Draught proofing | 1 | 1 | 1
Other | HW Tank insulation | HW Tank insulation | HW tank insulation | 1 | 1 | 1
Performance Gap Uplift
| Closure | 33.33% | 50% | 33.33% | 33.33% | 50% |  | * Based on Table 6 of the 5CB report: Review of potential for carbon savings from residential energy efficiency (2013). https://www.theccc.org.uk/wp-content/uploads/2013/12/Review-of-potential-for-carbon-savings-from-residential-energy-efficiency-Final-report-A-160114.pdf
Measure | IUF * | Widespread Engagement | Widespread Innovation | Headwinds | Balanced Net Zero Pathway | Tailwinds
Behavioural | 0% | 100% | 100% | 100% | 100% | 100%
Cavity wall | 35% | 117.9% | 126.9% | 117.9% | 117.9% | 126.9%
Solid wall | 33% | 116.4% | 124.6% | 116.4% | 116.4% | 124.6%
Roof | 35% | 117.9% | 126.9% | 117.9% | 117.9% | 126.9%
Floor | 15% | 105.9% | 108.8% | 105.9% | 105.9% | 108.8%
Glazing | 15% | 105.9% | 108.8% | 105.9% | 105.9% | 108.8%
Other | 15% | 105.9% | 108.8% | 105.9% | 105.9% | 108.8%
Supplementary Costs (mapping)
Supplementary Costs
Unit | Fixed £/house | Fixed £/house
Cost Item | Scaffolding - associated with external walls (insulation) only | Survey and Design
Measure / Cost Type | Construction Overheads | Design & Plannning
External (solid) wall insulation | 1 | 1
Internal (solid) wall insulation |  | 1
Financial Year Deflator
Source: CCC economic assumptions.
Calendar year | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019
GDP deflator at 2019 = 1 | 68.7 | 69.4 | 70.9 | 72.5 | 74.3 | 76.2 | 78.3 | 80.3 | 82.7 | 84 | 85.3 | 87.1 | 88.5 | 90.2 | 91.8 | 92.4 | 94.3 | 96.1 | 98.2 | 100
Applicablity of other Measures
Measure | Size | % of Stock | Source
Insulated doors | S | 56.44% | Based on 5CB technical potential distribution: Review of potential for carbon savings from residential energy efficiency (2013). https://www.theccc.org.uk/wp-content/uploads/2013/12/Review-of-potential-for-carbon-savings-from-residential-energy-efficiency-Final-report-A-160114.pdf
Draught proofing (draught stripping) | S | 85.22%
Reduced infiltration (foam, strips, sealent use) | S | 13.4%
HW Tank insulation | S | 0.08044%
Suspended timber floor insulation | S | 8.19%
Solid floor insulation | S | 22.72%
Insulated doors | M | 36.39%
Draught proofing (draught stripping) | M | 85.01%
Reduced infiltration (foam, strips, sealent use) | M | 6.449%
HW Tank insulation | M | 0.1248%
Suspended timber floor insulation | M | 28.22%
Solid floor insulation | M | 58.24%
Insulated doors | L | 35.2%
Draught proofing (draught stripping) | L | 84.56%
Reduced infiltration (foam, strips, sealent use) | L | 4.288%
HW Tank insulation | L | 0.08713%
Suspended timber floor insulation | L | 12.79%
Solid floor insulation | L | 65.78%